## 5. Oct 2018 R5 PWS with Pb ALE
State | PWSID | PWS Name | PWS Type Code | PWS Activity Code | Population Served Count | Link to Pb ALEs | Is School or Daycare? | On list in April 2018 ALE Attachment? | Reason for Update on System's Pb ALEs Based on July 2018 State Comments for existing ALEs and/or New ALEs in October 2018 Data Freeze (List of Reasons: New, Not Resolved, or New & Not Resolved) | January 2019 Summary Status Update from State (October 2018 ETT) | FYI Only: Region 5 Follow-up Items - September 2018; Addressed previously through calls and/or written follow-up. | July 2018 Summary Status Update from State (April 2018 ETT) | January 2018 Summary Status Update from State (October 2017 ETT) | July 2017 Summary Status from State (April 2017 ETT) | January 2017 Summary Status from State (October 2016 ETT) | June 2016 Summary Status from State | February 2016 Summary Status from State | February 2016 Detailed System Status
MI | MI0000125 | ALLEGAN COUNTY SERVICES CENTER | CWS | A | 101 | ALEs | N | Y |  |  | [multiple historical ALEs] |  |  | ALE resolved with sampling
MI | MI0000324 | AUSABLE VALLEY COMMUNITY | CWS | A | 147 | ALEs | N | Y |  |  | [multiple historical ALEs] |  |  | ALE resolved with sampling | 6. ALE Not Resolved – PWS has Current ALE | 6. ALE Not Resolved – PWS has Current ALE | Not Resolved | Existing corrosion control strategy insufficient and being re‐evaluated. Supply required by MDEQ to submit a revised corrosion control study and recommendations by March 31, 2016.
MI | MI0000690 | BEVERLY HILLS | CWS | A | 10451 | ALEs | N | Y | Not Resolved | 8. ALE not Resolved – Awaiting Sample Results – Most Recent 6M Round does not exceed AL | Has LSLR been conducted at 7%/year? | 5. ALE Not Resolved – Awaiting Sample Results
MI | MI0000877 | BRILEY TOWNSHIP | CWS | A | 435 | ALEs | N |  | New | 7. ALE not Resolved – Awaiting Sample Results – No Results Reported Yet
MI | MI0000930 | BROWN CITY | CWS | A | 1316 | ALEs | N |  | N/A | 1. PWS did not have a Pb ALE
MI | MI0001353 | CHATEAUX DU LAC CONDOMINIUMS | CWS | A | 80 | ALEs | N | Y |  |  | [multiple historical ALEs] |  |  | ALE resolved with fixture replacement and sampling. | 6. ALE Not Resolved – PWS has Current ALE | 6. ALE Not Resolved – PWS has Current ALE | Not Resolved | Corrosion control treatment permit issued November 2015. Supply working with contractor to complete treatment installation in early 2016. MDEQ Update 7/2017: Treatment is available, but not currently in use because supply resolved issue through fixture
MI | MI0001666 | CROOKED RIVER APARTMENTS | CWS | A | 32 | ALEs | N | Y |  |  | [multiple historical ALEs] |  |  |  |  | 3. ALE Resolved with Sampling
MI | MI0001932 | EAGLE VILLAGE | CWS | A | 84 | ALEs | N | Y | [7 empty] | 3. ALE Resolved with Sampling
MI | MI0002277 | LAKE PARK VILLAGE CONDOMINIUMS | CWS | A | 900 | ALEs | N | Y | Not Resolved | 8. ALE not Resolved – Awaiting Sample Results – Most Recent 6M Round does not exceed AL |  | 5. ALE Not Resolved – Awaiting Sample Results
MI | MI0002310 | FLINT, CITY OF | CWS | A | 98310 | ALEs | N | Y | [5 empty] | ALE resolved with Treatment | 6. ALE Not Resolved – PWS has Current ALE
MI | MI0003115 | HEMINGWAY POINTE CLUB OWNERS ASSOCIATION | CWS | A | 250 | ALEs | N | Y |  |  | [multiple historical ALEs] |  |  |  |  | 3. ALE Resolved with Sampling
MI | MI0003120 | HERMANSVILLE HOUSING COMM. | CWS | A | 36 | ALEs | N | Y | New & Not Resolved | 6. ALE not Resolved – Conducting CCT Steps to Resolve with Treatment | Why was a CCS, or some other corrective action, not required/conducted? [SDWIS-Fed shows previous historical ALE in 2014-2016, as well as a subsequent ALE in J-J 2018] | 5. ALE Not Resolved – Awaiting Sample Results
MI | MI0003230 | HOUGHTON | CWS | A | 7512 | ALEs | N | Y | Not Resolved | 4. ALE Resolved with Corrective Action followed by Sampling |  | 5. ALE Not Resolved – Awaiting Sample Results
MI | MI0003460 | ITHACA, CITY OF | CWS | A | 3098 | ALEs | N |  | N/A | 1. PWS did not have a Pb ALE
MI | MI0003666 | KNORRWOOD KNOLLS SUBDIVISION | CWS | A | 183 | ALEs | N | Y |  |  | (1) Why was a CCS not conducted for the J-J 2017 ALE? [note, previous historical ALE in 2013-2015] Was this due to equivalent action - e.g. adjusting phosphate-based CCT? (2) Is 0-11.27 mg/L correct for the orthophosphate d | 3. ALE Resolved with Sampling | 6. ALE Not Resolved – Conducting Corrosion Control Study |  | 3. ALE Resolved with Sampling | 6. ALE Not Resolved – PWS has Current ALE | Not Resolved | First round of increased monitoring was below action level. Second round due by June 30, 2016.
MI | MI0003685 | L'ARBRE CROCHE CLUB | CWS | A | 330 | ALEs | N | Y | [7 empty] | 3. ALE Resolved with Sampling
MI | MI0003820 | LAWRENCE | CWS | A | 1045 | ALEs | N |  | New | 7. ALE not Resolved – Awaiting Sample Results – No Results Reported Yet
MI | MI0003942 | ISLAND LAKE APARTMENTS | CWS | A | 46 | ALEs | N | Y | resolved | 3. ALE Resolved with Sampling | (1) Was it the same sample site that exceeded both times? [2 ALEs - in 2014-2016 and in J-J 2017] (2) Why was a CCS, or some other corrective action, not required/ conducted? | 5. ALE Not Resolved – Awaiting Sample Results | 6. ALE Not Resolved – Conducting Corrosion Control Study
MI | MI0004730 | NEWBERRY CORRECTIONAL FACILITY | CWS | A | 1001 | ALEs | N | Y |  |  | [multiple historical ALEs] |  |  |  |  | 4. ALE Resolved with Treatment
MI | MI0005268 | PERE MARQUETTE TWP - WELLS | CWS | A | 290 | ALEs | N | Y |  |  | [multiple historical ALEs] - This row seems to have been incorrectly included as active in Tab 5 - the only listed ALEs in Tab 6 are from 2007 and 2012-2014. | 3. ALE Resolved with Sampling
MI | MI0005785 | ROMULUS | CWS | A | 23989 | ALEs | N | Y | resolved | 3. ALE Resolved with Sampling | (1) Has LSLR been conducted at 7%/year? (2) Is CCS and/or CCT adjustments still going to be completed if 2 six-month rounds come back below the ALs? [note 4 historical ALEs in 1992 and 1997] | 5. ALE Not Resolved – Awaiting Sample Results | 5. ALE Not Resolved – Awaiting Sample Results
MI | MI0006042 | SHERWOOD SHORES CONDOMINIUMS | CWS | A | 90 | ALEs | N | Y | New & Not Resolved | 8. ALE not Resolved – Awaiting Sample Results – Most Recent 6M Round does not exceed AL | What is the goal of “investigative sampling”? To identify plumbing replacement needs? [note subsequent ALE in J-J 2018] | 5. ALE Not Resolved – Awaiting Sample Results
MI | MI0006110 | SOUTH LYON, CITY OF | CWS | A | 11055 | ALEs | N | Y | [7 empty] | 3. ALE Resolved with Sampling | Sampled Out | The City of South Lyon is not currently exceeding the lead action level. South Lyon did exceed the action level in 2013 (already had corrosion control treatment in place), but have since conducted 3 rounds of monitoring and all 3 were below the lead acti
MI | MI0006232 | SPRING LAKE CLUB CONDOMINIUMS | CWS | A | 87 | ALEs | N | Y |  |  | [multiple historical ALEs] |  |  |  |  | 3. ALE Resolved with Sampling
MI | MI0006575 | SUGARTREE APARTMENTS | CWS | A | 375 | ALEs | N | Y | [6 empty] | 3. ALE Resolved with Sampling | 6. ALE Not Resolved – PWS has Current ALE | Not Resolved | Supply conducted two rounds of increased monitoring and both were below the action level. However, review of the second round indicated some samples were taken at improper sites. MDEQ is requiring two additional rounds of increased monitoring at proper is
MI | MI0006792 | V F W NATIONAL HOME | CWS | A | 150 | ALEs | N | Y | Resolved | 4. ALE Resolved with Corrective Action followed by Sampling | Is the reported range (0.35 to 3.3 ppm) for orthophosphate reflective of the actual dosage before cleaning the injection port? Has the system subsequently maintained tighter process control? [note 6 historical ALEs in 1994-2004, as well as subsequent ALE | 5. ALE Not Resolved – Awaiting Sample Results | 5. ALE Not Resolved – Awaiting Sample Results
MI | MI0040028 | VILLAGE EAST ESTATES | CWS | A | 235 | ALEs | N | Y | Resolved | 3. ALE Resolved with Sampling |  | 5. ALE Not Resolved – Awaiting Sample Results
MI | MI0040090 | TWIN PINES MOBILE HOME PARK | CWS | A | 182 | ALEs | N | Y | [6 empty] | 3. ALE Resolved with Sampling | 6. ALE Not Resolved – PWS has Current ALE | Not Resolved | Exceedance determined December 2015 after MDEQ removed one low sample result due to analytical hold time exceedance. First round of increased monitoring due by June 30, 2016.
MI | MI0040217 | MAPLEVIEW ESTATES | CWS | A | 93 | ALEs | N | Y | [7 empty] | 3. ALE Resolved with Sampling
MI | MI0040223 | ARBOR VILLAGE | CWS | A | 670 | ALEs | N | Y | Resolved | 5. ALE Resolved with Treatment | (1) Why was a CCS not conducted for the previous (2015-2017) ALE? [SDWIS-Fed shows previous historical ALE in 2006-2008] Was this due to equivalent action - e.g. starting phosphate-based CCT? (2) Does the 'other CCT' noted by the state ref | 5. ALE Not Resolved – Awaiting Sample Results | 5. ALE Not Resolved – Awaiting Sample Results
MI | MI0040319 | ALAN'S PARK - FOWLERVILLE | CWS | A | 498 | ALEs | N | Y | [6 empty] | 3. ALE Resolved with Sampling | 6. ALE Not Resolved – PWS has Current ALE | Not Resolved | First round of increased monitoring was below action level. Second round due by June 30, 2016.
MI | MI0040335 | HOLIDAY VILLAGE MOBILE HOME PARK | CWS | A | 185 | ALEs | N | Y | Resolved | 3. ALE Resolved with Sampling |  | 5. ALE Not Resolved – Awaiting Sample Results
MI | MI0040438 | FREELAND MOBILE HOME PARK | CWS | A | 280 | ALEs | N | Y | Resolved | 3. ALE Resolved with Sampling | What 'other CCT' was in place at the time of the ALE (e.g. blended phosphates)? Are there any plans to adjust CCT or conduct other corrective actions? | 5. ALE Not Resolved – Awaiting Sample Results
MI | MI0060425 | THORNAPPLE MANOR | CWS | A | 328 | ALEs | N | Y | Resolved | 4. ALE Resolved with Corrective Action followed by Sampling | [multiple historical ALEs, recent corrective action] | 5. ALE Not Resolved – Awaiting Sample Results | 5. ALE Not Resolved – Awaiting Sample Results
MI | MI0062841 | MEDILODGE OF STERLING | CWS | A | 84 | ALEs | N | Y |  |  |  |  | 3. ALE Resolved with Sampling
MI | MI0220075 | AUTRAIN-ONOTA PUBLIC SCHOOL | NTNCWS | A | 63 | ALEs | Y | Y | [7 empty] | 3. ALE Resolved with Sampling
MI | MI0320360 | EAST MARTIN CHRISTIAN SCHOOL | NTNCWS | A | 150 | ALEs | Y | Y | [7 empty] | 3. ALE Resolved with Sampling
MI | MI0320571 | KRUGER COMMODITIES | NTNCWS | A | 65 | ALEs | N | Y | Not Resolved | 7. ALE not Resolved – Awaiting Sample Results – No Results Reported Yet |  | 6. ALE Not Resolved – Conducting Corrosion Control Study | 6. ALE Not Resolved – Conducting Corrosion Control Study
MI | MI0320600 | B&G CUSTOM WORKS,INC. | NTNCWS | A | 30 | ALEs | N | Y | Confirm Resolved? | 8. ALE not Resolved – Awaiting Sample Results – Most Recent 6M Round does not exceed | Can the state explain the response "ALE resolved with sampling" given that only J-J 2018 results were available (need 2 6-month rounds below ALs]? | 3. ALE Resolved with Sampling | 6. ALE Not Resolved – Conducting Corrosion Control Study
MI | MI1320024 | DORIS KLAUSSEN DEV CENTER | NTNCWS | A | 260 | ALEs | Y | Y | [7 empty] | 3. ALE Resolved with Sampling
MI | MI1320042 | PURDY SCHOOL | NTNCWS | A | 274 | ALEs | Y | Y |  |  |  |  | 3. ALE Resolved with Sampling
MI | MI1420041 | KINCHELOE ELEMENTARY SCHOOL | NTNCWS | A | 330 | ALEs | Y | Y | [7 empty] | 3. ALE Resolved with Sampling
MI | MI1620082 | CHEBOYGAN AREA SCHOOLS ADMIN. BLDG. | NTNCWS | A | 40 | ALEs | Y | Y | [7 empty] | 3. ALE Resolved with Sampling
MI | MI1820020 | CLARE-GLADWIN RESD | NTNCWS | A | 118 | ALEs | Y | Y | Not Resolved | 8. ALE not Resolved – Awaiting Sample Results – Most Recent 6M Round does not exceed AL |  | 5. ALE Not Resolved – Awaiting Sample Results
MI | MI1820290 | Farwell Alternative Education | NTNCWS | A | 45 | ALEs | Y | Y | [7 empty] | 3. ALE Resolved with Sampling
MI | MI1920059 | RILEY ELEMENTARY SCHOOL | NTNCWS | A | 281 | ALEs | Y | Y | [7 empty] | 3. ALE Resolved with Sampling
MI | MI2320093 | DIMONDALE ELEMENTARY SCHOOL | NTNCWS | A | 320 | ALEs | Y | Y | [5 empty] | ALE resolved with sampling | 6. ALE Not Resolved – PWS has Current ALE | 6. ALE Not Resolved – PWS has Current ALE | Not Resolved | Using bottled water. Water supply owner started investigative sampling, started replacing fixtures. MDEQ will conduct a site visit in January 2016 to walk through entire school and observe fixture replacement and discuss future sampling.
MI | MI2320294 | POLLY PRODUCTS ALR, LLC | NTNCWS | A | 35 | ALEs | N | Y |  |  |  |  | 3. ALE Resolved with Sampling | ALE Not Resolved - PWS has current ALE
MI | MI2520452 | DIECK ELEMENTARY | NTNCWS | A | 326 | ALEs | Y | Y | Not Resolved | 3. ALE Resolved with Sampling |  | 5. ALE Not Resolved – Awaiting Sample Results
MI | MI2820036 | FIFE LAKE ELEMENTARY SCHOOL | NTNCWS | A | 166 | ALEs | Y | Y | [5 empty] | ALE resolved with sampling
MI | MI3020031 | NORTH ADAMS PUBLIC SCHOOLS | NTNCWS | A | 350 | ALEs | Y | Y | [7 empty] | 3. ALE Resolved with Sampling
MI | MI3320169 | VLAHAKIS MANAGEMENT COMPANY | NTNCWS | A | 100 | ALEs | Y | Y | [5 empty] | ALE resolved with Treatment | 6. ALE Not Resolved – PWS has Current ALE | 6. ALE Not Resolved – PWS has Current ALE | Not Resolved | Day care using bottled water. DEQ Administrative Consent Order signed by Vlahakis, July 29, 2015. DEQ determined stipulations of the ACO were not met as of October 23, 2015. MDEQ met with owner on‐site December 29, 2015 to discuss treatment options. T
MI | MI3320180 | Colt's and Filly's Childcare | NTNCWS | A | 132 | ALEs | Y | Y | [7 empty] | 3. ALE Resolved with Sampling
MI | MI3420086 | EIGHT CAP IONIA CO. OUTREACH | NTNCWS | A | 33 | ALEs | Y | Y | Not Resolved | 4. ALE Resolved with Corrective Action followed by Sampling |  | Based on MDEQ responses in Tab 6, "Not resolved - Awaiting sampling results" |  |  |  | 3. ALE Resolved with Sampling | Not Resolved | Day care using bottled water. The hallway drinking fountain with high lead levels has been removed. Second round of increased monitoring due June 30, 2016.
MI | MI3420231 | FAITH COMMUNITY CHRISTIAN SCH. | NTNCWS | A | 56 | ALEs | Y | Y | [6 empty] | 3. ALE Resolved with Sampling | 6. ALE Not Resolved – PWS has Current ALE | Not Resolved | Offending fixtures have been replaced. First round of increased monitoring due June 30, 2016. First round of sampling completed on 6/2/2016 and results are below 90th percentile. Second round of samples collected on 9/7/2016 and 9/8/2016 and results a
MI | MI3920018 | Lakeland Reformed Church | NTNCWS | A | 125 | ALEs | Y | Y | [7 empty] | 3. ALE Resolved with Sampling
MI | MI4120203 | WHITE EARLY CHILDHOOD CENTER | NTNCWS | A | 60 | ALEs | Y | Y | Not Resolved | 4. ALE Resolved with Corrective Action followed by Sampling |  | 5. ALE Not Resolved – Awaiting Sample Results
MI | MI4120793 | MAGNA MIRRORS | NTNCWS | A | 550 | ALEs | N | Y | [7 empty] | 4. ALE Resolved with Treatment
MI | MI4120810 | MAST YOUNG PLANTS | NTNCWS | A | 150 | ALEs | N | Y |  |  |  |  | 3. ALE Resolved with Sampling
MI | MI4121001 | SPEEDRACK MIDWEST | NTNCWS | A | 41 | ALEs | N | Y | Not Resolved | 4. ALE Resolved with Corrective Action followed by Sampling |  | 5. ALE Not Resolved – Awaiting Sample Results | 6. ALE Not Resolved – Conducting Corrosion Control Study
MI | MI4520028 | BLUEBIRD RESTAURANT & BAR | NTNCWS | A | 450 | ALEs | N | Y | [5 empty] | ALE Resolved with fixture replacement and sampling.TB | 6. ALE Not Resolved – PWS has Current ALE | 6. ALE Not Resolved – PWS has Current ALE | Not Resolved | Supply owner disconnected the service bar sink that was exceeding. First round of increased monitoring was below action level. Second round samples were required to be collected before December 31, 2015, but were not collected until the week of January
MI | MI4720157 | PINCKNEY SCHOOLS - PATHFINDER SCHOOL | NTNCWS | A | 550 | ALEs | Y | Y |  |  | [multiple historical ALEs] |  | 3. ALE Resolved with Sampling | ALE not resolved - PWS has current ALE.
MI | MI4720357 | PINCKNEY SCHOOLS - COUNTRY ELEMENTARY | NTNCWS | A | 339 | ALEs | Y | Y |  |  | [multiple historical ALEs] |  |  |  |  | 3. ALE Resolved with Sampling
MI | MI4720763 | THE RE/MAX BUILDING | NTNCWS | A | 200 | ALEs | N | Y |  |  |  |  | 3. ALE Resolved with Sampling | ALE Not Resolved - PWS has Current ALE
MI | MI5220042 | Silver Creek Church | NTNCWS | A | 29 | ALEs | Y | Y |  |  |  | 3. ALE Resolved with Sampling | 5. ALE Not Resolved – Awaiting Sample Results | ALE not resolved - PWS has current ALE. Well replaced but samples still continue to exceed ALE. RW
MI | MI5220072 | Tilden Pit Service Building (old Empire) | NTNCWS | A | 409 | ALEs | N | Y |  |  |  | 3. ALE Resolved with Sampling | 5. ALE Not Resolved – Awaiting Sample Results | ALE not resolved - PWS has current ALE. Fixtures replaced but samples still continue to exceed ALE. RW
MI | MI5220151 | Reinhart Instutional Foods | NTNCWS | A | 38 | ALEs | N | Y | [5 empty] | ALE resolved with fixture replacement and sampling. RW |  | 3. ALE resolved with sampling.
MI | MI5420437 | US MARBLE | NTNCWS | A | 25 | ALEs | N | Y |  |  |  |  | 3. ALE Resolved with Sampling
MI | MI5720056 | FALMOUTH PRESCHOOL | NTNCWS | A | 25 | ALEs | Y | Y | Not Resolved | 4. ALE Resolved with Corrective Action followed by Sampling |  | Based on MDEQ responses in Tab 6, "Not resolved - conducting CCS" | 5. ALE Not Resolved – Awaiting Sample Results
MI | MI5820156 | WHITEFORD HIGH SCHOOL | NTNCWS | A | 446 | ALEs | Y | Y |  |  |  |  | 3. ALE Resolved with Sampling
MI | MI5820388 | BIG DADDY'S TRUCK STOP | NTNCWS | A | 500 | ALEs | N | Y | [7 empty] | 3. ALE Resolved with Sampling
MI | MI5920043 | VESTABURG HIGH SCHOOL | NTNCWS | A | 300 | ALEs | Y | Y | [7 empty] | 3. ALE Resolved with Sampling
MI | MI6020023 | LEWISTON K-6 SCHOOL | NTNCWS | A | 300 | ALEs | Y | Y | [7 empty] | 3. ALE Resolved with Sampling
MI | MI6220059 | NEWAYGO CHILD DEVELOPMENT CENTER | NTNCWS | A | 50 | ALEs | Y | Y | Not Resolved | 4. ALE Resolved with Corrective Action followed by Sampling |  | Based on MDEQ responses in Tab 6, "Not resolved - conducting CCS" | 5. ALE Not Resolved – Awaiting Sample Results
MI | MI6320778 | BAILEY LAKE ELEM SCHOOL/CCS | NTNCWS | A | 600 | ALEs | Y | Y |  |  |  |  | 3. ALE Resolved with Sampling | ALE not resolved. PWS has current ALE - Fixtures replaced and retested. Waiting for two semi annual sets to SOX violation.
MI | MI6320790 | OAKLAND SCHOOLS-TECHNICAL CAMPUS NW | NTNCWS | A | 500 | ALEs | Y | Y | [7 empty] | 3. ALE Resolved with Sampling
MI | MI6320792 | ANDERSONVILLE ELEM/CCS | NTNCWS | A | 400 | ALEs | Y | Y | [7 empty] | 3. ALE Resolved with Sampling
MI | MI6320797 | AUTOMATION & MODULAR COMPONENTS | NTNCWS | A | 70 | ALEs | N | Y | Confirm Resolved? | 4. ALE Resolved with Corrective Action followed by Sampling |  | Based on MDEQ responses in Tab 6, "ALE Resolved with Sampling" following fixture replacement. | ALE Not Resolved - Awaiting Sampling Results. Sampled 9/2017. Need second six month sample Jan-June 2018 before being SOXed.
MI | MI6321388 | EPIC LIFE CHURCH | NTNCWS | A | 200 | ALEs | Y | Y |  |  |  |  | 3. ALE Resolved with Sampling
MI | MI6322144 | SPRINGFIELD PLAINS ELEMENTARY | NTNCWS | A | 600 | ALEs | Y | Y |  |  |  |  | 3. ALE Resolved with Sampling | ALE not resolved. PWS has current ALE - Fixtures replaced and retested. Waiting for two semi annual sets to SOX violation.
MI | MI6322603 | GANEINU DAY SCHOOL | NTNCWS | A | 50 | ALEs | Y | Y |  |  |  |  | 3. ALE Resolved with Sampling | ALE not resolved. PWS has current ALE - Fixtures replaced and retested. Waiting for two semi annual sets to SOX violation.
MI | MI6520157 | OGEMAW HEIGHTS HIGH SCHOOL | NTNCWS | A | 706 | ALEs | Y | Y | [7 empty] | 3. ALE Resolved with Sampling | Not Resolved | School conducting a treatment study, removing fixtures, and re‐sampling. School also implemented a routine flushing program throughout the building. Next required sampling due by June 2016. The 90th percentiles of the last three 6 month rounds of sampl
MI | MI6720085 | NARTRON CORP. | NTNCWS | A | 40 | ALEs | N | Y | Not Resolved | 8. ALE not Resolved – Awaiting Sample Results – Most Recent 6M Round does not exceed AL |  | 5. ALE Not Resolved – Awaiting Sample Results | 5. ALE Not Resolved – Awaiting Sample Results | ALE Not Resolved - PWS has current ALE
MI | MI7020398 | CONSUMERS ENERGY WELLS 4,6, & 17 | NTNCWS | A | 600 | ALEs | N | Y | Not Resolved | 6. ALE Not Resolved – Conducting Corrosion Control Study | [note historical ALE in 2010] | 6. ALE Not Resolved – Conducting Corrosion Control Study | 6. ALE Not Resolved – Conducting Corrosion Control Study | 6. ALE Not Resolved – PWS has Current ALE
MI | MI7220146 | ROSCOMMON HIGH SCHOOL | NTNCWS | A | 435 | ALEs | Y | Y | Not Resolved | 3. ALE Resolved with Sampling |  | Based on MDEQ responses in Tab 6, "Not resolved - conducting CCS"
MI | MI7320187 | SAINT MICHAELS CHURCH | NTNCWS | A | 250 | ALEs | Y | Y | Confirm Resolved? | 4. ALE Resolved with Corrective Action followed by Sampling |  | Based on MDEQ responses in Tab 6, "ALE Resolved with Sampling" following fixture replacement. | 5. ALE Not Resolved – Awaiting Sample Results | ALE Not Resolved - PWS has current ALE
MI | MI7520157 | MICHIGAN MILK PRODUCERS ASSOC | NTNCWS | A | 51 | ALEs | N | Y |  |  |  | 3. ALE Resolved with Sampling
MI | MI8020265 | COCA COLA REFRESHMENTS | NTNCWS | A | 540 | ALEs | N | Y |  |  | [multiple historical ALEs] |  | 3. ALE Resolved with Sampling | ALE Not Resolved - PWS has current ALE | 6. ALE Not Resolved – PWS has Current ALE | 6. ALE Not Resolved – PWS has Current ALE |  | CHK transferred oversight of system to KH.
MI | MI8020269 | BLOOMINGDALE HIGH SCHOOL | NTNCWS | A | 425 | ALEs | Y | Y |  |  |  |  | 3. ALE Resolved with Sampling
MI | MI8320059 | WEXFORD MISSAUKEE CAREER TECH CENTER | NTNCWS | A | 550 | ALEs | Y | Y | [7 empty] | 3. ALE Resolved with Sampling

## 6. Oct 2018 R5 Pb ALE Data
Newly reported Pb ALEs from October 2018 SDWIS/Fed; Plus historical Pb ALEs of interest | [10 empty] | FYI ONLY - Older info provided in 2018 by States and/or R5 - FYI ONLY | [17 empty] | FYI ONLY - Older info provided in 2016 - 2017 by States and/or R5 - FYI ONLY
PWSID | PWS Name | Primacy Agency | Contaminant Name | Pb 90th Percentile in mg/L | Pb 90th Percentile converted to ug/L | SDWIS/Fed Compliance Period Begin Date | SDWIS/Fed Compliance Period End Date | SDWIS/Fed First Reported Date | SDWIS/Fed Last Reported Date | R5 Notes | Is this Pb ALE Resolved Based on January 2018 State Responses? | 1_ Is this Pb ALE valid? (Y/N) (e_g_, data entry error) | 2_ Number of samples, and levels (in ppb) of samples above 15 ppb for this Pb ALE | 3_ Was Public Education completed for this Pb ALE? (Y/N) | 4_ Was lead consumer notice provided for this Pb ALE? (Y/N) | 5_ Is the system taking any actions after the Pb ALE in addition to standard 6-month LCR compliance monitoring? (Y/N) | 6_ Does the PWS have lead service lines (LSLs) in the publicly-owned portion of the distribution system? (Y/N/UNKNOWN) | 7_ Does the PWS have LSLs in the privately-owned portion of the distribution system? (Y/N/UNKNOWN) | 8_ What, if any, corrosion control treatment (CCT) was in place at the time of this Pb ALE? (Drop Down list: 1_ pH/Alkalinity adjustment, 2_ Orthophosphate, 3_ Silicate, 4_ Other, or 5_ None) | 9_ What is the pH range(s) at the entry point(s) to the distribution system (EPTDS), (e_g_, during monitoring period with ALE)? | 10_ If orthophosphate is added, what are the orthophosphate levels at the EPTDS(s), (e_g_, during monitoring period with ALE)? | 11_ Did the state require the system to perform a corrosion control study (CCS) after this Pb ALE? (Y/N) | 12_ Is a CCS underway or pending? (Y/N) | 13_ Is the PWS replacing plumbing? (Y/N) | 14_ For system with CCT: Is PWS implementing a LSL replacement program after ALE? (Y/N) | 15_ Date this Pb ALE was resolved | 16_ What other actions were taken at PWS (e_g_, alternate water provided, filters)? | 17_ Comments (other information) | FYI ONLY - November 2017: R5 Follow-up Questions based on July 2017 State Responses to April 2017 SDWIS FREEZE | July 2017 State Response to EPA May 2017 Questions to the right | MAY 2017: R5 Follow-up Questions for State based on January 2017 | 1_ Is this Lead (Pb) ALE valid? (Y/N) (e_g_, data entry error) | 2_ State Monitoring Period for this Pb ALE | 3_ Were any samples invalidated? (Y/N) If Yes, sample invalidati | 4_ Number of samples, and levels (in ppb) of samples above 15 pp | 5_ Was Public Education timely for this Pb ALE? (Y/N) (i_e_, wit | 6_ Date PE completed for this Pb ALE | 7_ Was lead consumer notice provided for this Pb ALE? (Y/N) | 8_ Date lead consumer notice certified to State for this Pb ALE | 9_ For small/med systems: Was a corrosion control study (CCS) in | 10_ CCT Study underway or pending? (Y/N) | 11_ Date CCS completed | 12_ Corrosion Control Treatment Installed or Installing/WQP? (Y/ | 13_ Date CCT installed | 14_ Replacing Plumbing? (Y/N) | 15_ For system with CCT: Is PWS implementing a LSL replacement p | 16_ Date the Pb ALE was resolved_ | 17_ Other actions taken at PWS (e_g_, alternate water provided, | 18_ Comments (other information)
MI0000125 | ALLEGAN COUNTY SERVICES CENTER | MI | LEAD SUMMARY | 0.027 | 27 | 2016-01-01 | 2016-12-31 | 2016-12-02 14:11 | 2018-03-22 13:44 |  | Yes | [17 empty] | Based on responses to PE Questions, it appears a PE (Type 65) violation should have been entered into SDWIS. |  |  | Y | June to Sept. 2016 | N | 7 samples: 29, 21, 20, 110, 35, 16, 160 ppb | Y | 3/1/2017 | Y | 11/14/2016 | N | N | N/A | N | N. | Y | N/A | 6/27/2017 |  | Supply replaced all in-building plumbing and fixtures, and re-assessed their sampling pool. 1st round of 2017 was below the AL. 2nd round due by 12/31/17.
MI0000324 | AUSABLE VALLEY COMMUNITY | MI | LEAD SUMMARY | 0.0676 | 67.6 | 2015-01-01 | 2015-12-31 | 2015-11-27 13:40 | 2018-03-26 12:54 |  | Yes | [20 empty] | Y | June to Sept, 2015 | N | 3 smpls: 31, 92, & 266 ppb | Y | 11/13/2015 | Y | 11/15/2015 | Yes, however original CCS was insufficient. DEQ required a revised plan be submitted. | complete | revised copy submitted 6/30/2016 | N/Y | n/a | Unknown | N | has not yet | Supply adjusted treatment and completed fixture replacement. 1st round in 2017 had AL of 0 ppb. Next round due by 12/31/17. | DEQ is currently reviewing the CCS. The system did collect another round on 11/1/16, which was at 15 ppb. Though the system currently has 2 rounds at or below the AL, the DEQ is requiring the sypply to continue towards installing CCT, since they have
MI0000324 | AUSABLE VALLEY COMMUNITY | MI | LEAD SUMMARY | 0.017 | 17 | 2013-01-01 | 2013-06-30 | 2013-08-20 12:43 | 2018-03-26 12:54 |  | Yes | [20 empty] | Y | 1/1/13 - 6/30/13 | N | 2 smpls: 17 & 44 ppb | Y | 8/14/2013 | Y | 7/5/2013 | Y | complete | 6/30/2016 | N/Y | n/a | Unknown | N |  |  | See above. DEQ letter indicated that AVC must either improve its ability to control over-softening or install a different type of treatment.
MI0000324 | AUSABLE VALLEY COMMUNITY | MI | LEAD SUMMARY | 0.0175 | 17.5 | 2008-01-01 | 2010-12-31 | 2011-02-24 08:40 | 2018-03-26 12:54 |  | Yes | [18 empty] | MDEQ 7/17 - 2010 was first year of this requirement. State was disinvested in following up on these when no sample over AL. This violation was apparently missed. | Based on responses to Questions 7 and 8, a LCR (Type 66) violation should have been reported to SDWIS. November 2017 R5 follow-up correction: Disregard this question because the first standard and reduced Lead and Copper monitoring periods that the LCN re | Y | June to Sept, 2010 | N | 2 smpls: 17 & 18 ppb | N - late | 1/5/2011 | N |  | Y | complete | 6/30/2016 | Y/Y | 1/16/2013 | unknown | N |  | Supply was over-softening, decided to do controlled softening. | See above.
MI0000690 | BEVERLY HILLS | MI | LEAD SUMMARY | 0.0913 | 91.3 | 2015-01-01 | 2017-12-31 | 2017-11-29 16:23 | 2018-03-26 12:54 |  |  | Y | 1 sample - 228.26 ppb | Y | Y | Y | Y | Y | 2. Orthophosphate | Springwells: 7.05 to 7.37 Northeast: 7.12 to 7.39 | Springwells: 0.9 to 3.42 ppm Northeast: 0.81 to 1.39 ppm | N | Y | Y | Y |  | Immediately replaced LSL at high site | OCCT provided by seller to this community, not by the community itself.
MI0000817 | BOYSVILLE | MI | LEAD SUMMARY | 0.026 | 26 | 2014-07-01 | 2014-12-31 | 2015-02-26 15:38 | 2018-03-26 12:54 |  | Yes | [17 empty] | Based on the responses to LCN questions, a LCN (Type 66) violation should have been entered into SDWIS. | MDEQ 7/17 - Due to resource limitations, violations for late reporting were not issued. | Based on responses to Questions 7 and 8, a LCR (Type 66) violation should have been reported to SDWIS. | Y | 7/1/14 - 12/31/14 | N | 1 smpl: 47 ppb | N - late | 2/5/2015 | Y | 1/26/2016 | Not a treatment study | N | n/a | No/Yes | n/a | may | N | 6/29/2016 | providing bottled water to staff | System collected 2nd 6 month round on 6/29/16, with an AL 90th of 2 ppb. System is not currently serving residential customers. It was adding phosphate for iron and turned it off without approval. Shortly after the facility was vacated by all but staff.
MI0000877 | BRILEY TOWNSHIP | MI | LEAD SUMMARY | 0.024 | 24 | 2016-01-01 | 2018-12-31 | 2018-08-29 10:28 |  | Newly reported (after April 2018 freeze)
MI0000930 | BROWN CITY | MI | LEAD SUMMARY | 0.02 | 20 | 2016-01-01 | 2018-12-31 | 2018-08-29 10:28 |  | Newly reported (after April 2018 freeze)
MI0001353 | CHATEAUX DU LAC CONDOMINIUMS | MI | LEAD SUMMARY | 0.079 | 79 | 2014-07-01 | 2014-12-31 | 2015-05-22 14:12 | 2018-03-20 11:53 |  | Yes | [17 empty] | Based on responses to PE Questions, it appears a PE (Type 65) violation should have been entered into SDWIS. | MDEQ 7/17 - Supply was issuing PE on an annual basis to residents. Due to resource limitations, violations for late reporting were not issued. | Based on responses to Questions 5 and 6, a PE (Type 65) violation should have been reported to SDWIS. | Y | 7/1/14 - 12/31/14 | N | 1 smpl: 188 ppb | Not all were completed within 60 days; however, supply was providing complete PE with CCR each year. | 7/3/2015 | Y | 11/19/2014 | Not a treatment study | complete | 2/25/2014 | Y/Y | permit issued 11/17/15 | Proposed, see column 18 | n/a | has not yet | MDEQ 7/17: Supply made modifications to in-home treatment units which were bringing pH down to 5. Since then, first round of sampling below the AL, second round due by 12/31/17. | The DEQ is no longer requiring a Consent Order, but the supply is doing further investigation and mitigation at the individual homes with high results in an effort to bring the supply back into compliance. DEQ met with supply on 7/7/16. The treatment eq
MI0001353 | CHATEAUX DU LAC CONDOMINIUMS | MI | LEAD SUMMARY | 0.033 | 33 | 2013-01-01 | 2013-06-30 | 2014-02-12 15:54 | 2018-03-14 14:20 |  | Yes | [20 empty] | Y | 1/1/13 - 6/30/13 | N | 2 smpls: 51 & 85 ppb |  | 6/28/2013 & 6/30/14 | Y | 6/10/2013 | Not a treatment study | Y | 2/25/2014 | N/Y | n/a | N | N | has not yet |  | see above
MI0001353 | CHATEAUX DU LAC CONDOMINIUMS | MI | LEAD SUMMARY | 0.0395 | 39.5 | 2012-07-01 | 2012-12-31 | 2014-02-12 15:54 | 2018-03-15 10:55 |  | Yes | [17 empty] | Based on responses to PE Questions, it appears a PE (Type 65) violation should have been entered into SDWIS. | MDEQ 7/17 - Supply was issuing PE on an annual basis to residents. Due to resource limitations, violations for late reporting were not issued. | Based on responses to Questions 5 and 6, a PE (Type 65) violation should have been reported to SDWIS. | Y | 7/1/12 - 12/31/12 | N | 1 smpl: 74 ppb |  | 6/28/2013 | Y | 9/26/2012 | Y | Y | 2/25/2014 | N/Y | n/a | N | N | has not yet |  | see above
MI0001353 | CHATEAUX DU LAC CONDOMINIUMS | MI | LEAD SUMMARY | 0.025 | 25 | 2012-01-01 | 2012-06-30 | 2013-08-20 12:43 | 2018-03-14 14:20 |  | Yes | [20 empty] | Y | 1/1/12 - 6/30/12 | N | 2 smpls: 25 & 122 ppb |  | 6/29/2012 | Y | 7/27/2012 | Y | Y | 2/25/2014 | N/Y | n/a | N | N | has not yet |  | see above
MI0001353 | CHATEAUX DU LAC CONDOMINIUMS | MI | LEAD SUMMARY | 0.023 | 23 | 2011-01-01 | 2011-12-31 | 2014-02-12 15:54 | 2018-03-15 10:55 |  | Yes | [20 empty] | Y | June to Sept, 2011 | N | 1 smpl: 43 ppb |  | 6/27/2011 | Y | 10/26/2011 | N | N | 2/25/2014 | N/Y | n/a | N | N | has not yet |  | see above
MI0001353 | CHATEAUX DU LAC CONDOMINIUMS | MI | LEAD SUMMARY | 0.059 | 59 | 2008-01-01 | 2008-12-31 | 2009-08-19 14:55 | 2018-03-15 10:55 |  | Yes | [20 empty] | Y | June to Sept, 2008 | N |  | Y | 12/12/2008 | N | None | N | N | 2/25/2014 | N/Y | n/a | N | N | 12/31/2009 |  | see above
MI0001666 | CROOKED RIVER APARTMENTS | MI | LEAD SUMMARY | 0.0235 | 23.5 | 2010-01-01 | 2012-12-31 | 2013-02-26 14:09 | 2018-03-20 11:53 |  | Yes | [20 empty] | Y | June to Sept, 2012 | N | 2 smpls: 20 & 27 ppb | N - viol issued | 3/21/2013 | Y | 8/1/2012 | Not a treatment study | N | n/a | N | n/a | N | n/a | 1/1/2014 |  | Resolved
MI0001932 | EAGLE VILLAGE | MI | LEAD SUMMARY | 0.0188 | 18.8 | 2012-01-01 | 2014-12-31 | 2014-11-24 14:13 | 2018-03-15 10:55 |  | Yes | [17 empty] | Based on responses to PE Questions, it appears a PE (Type 65) violation should have been entered into SDWIS. | MDEQ 7/17 - Violation inadvertently missed. System did get 1 round of samples below AL before deadline for PE, therefore analyst may have determined PE no longer necessary. Analyst no longer with program. | Based on responses to Questions 5 and 6, a PE (Type 65) violation should have been reported to SDWIS. | Y | June to Sept, 2014 | N | 1 smpl: 71 ppb | N | 12/5/2014 | Y | 11/14/2014 | Not a treatment study | N | N/A | N | N/A | N | n/a | 7/1/2015 |  | Resolved
MI0002277 | LAKE PARK VILLAGE CONDOMINIUMS | MI | LEAD SUMMARY | 0.069 | 69 | 2015-01-01 | 2017-12-31 | 2017-11-29 16:23 | 2018-03-26 12:54 |  |  | Y | 2 samples - 69 ppb and 32 ppb | Y | Y | N | N | N | 5. None | 7.93 & 7.96 | n/a | N | N | N | N
MI0002310 | FLINT, CITY OF | MI | LEAD SUMMARY | 0.02 | 20 | 2016-01-01 | 2016-06-30 | 2016-09-27 13:59 | 2018-03-22 13:44 |  | Yes | [20 empty] | Y | 1/1/16 - 6/30/16 | Y - numerous for various reasons, ie inability to validate sampling technique, hold time, after filter, etc. | 88 out of 633 samples, results range from 16 ppb to 3343 ppb | Y | direct mailing & press release sent 8/18/16. Additional activities completed by 8/29/16. | Y | 8/18/2016 | N/A | Y | not yet | Yes, Currently customer of GLWA, who employs CCT. Also boosting phosphate at plant. /WQP done weekly. | supplimental 12/15/2016. GLWA in 1990s (as DWSD). | Y | Y | 1/23/2017 | Filters and bottled water being provided. | MDEQ 7/17: Supply has 1 round below AL. Continuing to work with MDEQ and EPA on resolutions to all issues. This is a complex, ongoing situation in which Region 5 is directly involved, and kept up to date on all activities being conducted. All this inf
MI0003115 | HEMINGWAY POINTE CLUB OWNERS ASSOCIATION | MI | LEAD SUMMARY | 0.0215 | 21.5 | 2012-01-01 | 2014-12-31 | 2014-11-24 14:13 | 2018-03-15 10:55 |  | Yes | [20 empty] | Y | June to Sept, 2014 | N | 2 smpls: 17 & 26 ppb | Y | 11/13/2014 | Y | 12/12/2014 | Not a treatment study | N | n/a | N | n/a | N | N | 7/1/2015 |  | Resolved
MI0003120 | HERMANSVILLE HOUSING COMM. | MI | LEAD SUMMARY | 0.023 | 23 | 2018-01-01 | 2018-06-30 | 2018-05-31 11:12 | 2018-08-29 10:28 | Newly reported (after April 2018 freeze)
MI0003120 | HERMANSVILLE HOUSING COMM. | MI | LEAD SUMMARY | 0.042 | 42 | 2017-07-01 | 2017-12-31 | 2017-11-29 16:23 | 2018-03-26 12:54 |  |  | Y | 1 SAMPLE - 78 ppb | Y | Y | N | N | N | 5. None | 7.5 | n/a | N | N | N | N
MI0003230 | HOUGHTON | MI | LEAD SUMMARY | 0.016 | 16 | 2015-01-01 | 2017-12-31 | 2017-11-29 16:23 | 2018-03-26 12:54 |  |  | Y | 3 Samples - 16 ppb, 20 ppb, and 21 ppb | Y | Y | Y | N | N | 1. pH/Alkalinity adjustment | 7.43 to 8.75 | n/a | N | N | N | N |  | Increased soda ash feed
MI0003460 | ITHACA, CITY OF | MI | LEAD SUMMARY | 0.031 | 31 | 2016-01-01 | 2018-12-31 | 2018-08-29 10:28 |  | Newly reported (after April 2018 freeze)
MI0003666 | KNORRWOOD KNOLLS SUBDIVISION | MI | LEAD SUMMARY | 0.02 | 20 | 2013-01-01 | 2015-12-31 | 2015-11-27 13:40 | 2018-03-20 11:53 |  | Yes
MI0003666 | KNORRWOOD KNOLLS SUBDIVISION | MI | LEAD SUMMARY | 0.022 | 22 | 2017-01-01 | 2017-06-30 | 2017-08-31 08:25 | 2018-03-26 12:54 |  | No | Y | 3 samples - 18 ppb, 39 ppb, 140 ppb | Y | Y | Y | N | N | 2. Orthophosphate | 7.90 & 7.95 | 0 to 11.27 ppm | N | N | N | N | 43269 | Increased inhibitor feed rate |  |  |  |  | Y | June to Sept, 2015 | N | 1 smpl: 40 ppb | Y | 11/9/2015 | Y | 1/4/2016 | Not a treatment study | N | n/a | N | n/a | N | n/a | 7/1/2016 |  | System now has 2 rounds below AL, resolved.
MI0003685 | L'ARBRE CROCHE CLUB | MI | LEAD SUMMARY | 0.034 | 34 | 2012-01-01 | 2014-12-31 | 2014-11-24 14:13 | 2018-03-15 10:55 |  | Yes | [20 empty] | Y | June to Sept, 2014 | N | 4 smpls: 21, 24, 34, & 36 ppb | Y | 9/22/2014 | Y | 9/9/2014 | Not a treatment study | N | n/a | N | n/a | N | N | 7/1/2015 |  | Resolved
MI0003820 | LAWRENCE | MI | LEAD SUMMARY | 0.024 | 24 | 2016-01-01 | 2018-12-31 | 2018-08-29 10:28 |  | Newly reported (after April 2018 freeze)
MI0003942 | ISLAND LAKE APARTMENTS | MI | LEAD SUMMARY | 0.082 | 82 | 2017-01-01 | 2017-06-30 | 2017-08-31 08:25 | 2018-03-26 12:54 |  | No | Y | 1 sample - 155 ppb | Y | Y | N | N | N | 5. None | not collected - monitoring violation issued | n/a | N | N | N | N |  |  | 2017-2 90th is 14 ppb. Waiting on 2nd set.
MI0003942 | ISLAND LAKE APARTMENTS | MI | LEAD SUMMARY | 0.037 | 37 | 2014-01-01 | 2016-12-31 | 2016-12-02 14:11 | 2018-03-22 13:44 |  | No | Y | 1 Sample - 72 ppb | Y | Y | N | N | N | 5. None | 7.78 | n/a | N | N | N | N
MI0004730 | NEWBERRY CORRECTIONAL FACILITY | MI | LEAD SUMMARY | 0.017 | 17 | 2012-07-01 | 2012-12-31 | 2013-02-26 14:09 | 2018-03-14 14:20 |  | Yes | [17 empty] | Based on the responses to LCN questions, a LCN (Type 66) violation should have been entered into SDWIS. | MDEQ 7/17 - Staff were in communication with the supply and determined PE had been issued, but MDEQ failed to retain documentation, therefore no violation issued. | Based on responses to Questions 7 and 8, a LCR (Type 66) violation should have been reported to SDWIS. | Y | 7/1/12 - 12/31/12 | N | 3 samples - 17, 20 & 74 ppb | Letter dated 1/23/2013 reports results for 12/18/2012 samples and 1/10/2013 samples - 20 each time and first half set of samples shows them back in compliance. Letter indicates Lead Ed is suspended at that time. | not in file | Unknown | not in file | Continue to feed blended polyphosphate. | N | n/a | y | Mar-12 | N | n/a | 12/31/2013 |  | 2 rounds in 2013 and 1 round in 2014 below AL. Resolved.
MI0004730 | NEWBERRY CORRECTIONAL FACILITY | MI | LEAD SUMMARY | 0.02 | 20 | 2012-01-01 | 2012-06-30 | 2012-08-28 10:11 | 2018-03-14 14:20 |  | Yes | [17 empty] | Based on the responses to LCN questions, a LCN (Type 66) violation should have been entered into SDWIS. | MDEQ 7/17 - Staff were in communication with the supply and determined PE had been issued, but MDEQ failed to retain documentation, therefore no violation issued. | Based on responses to Questions 7 and 8, a LCR (Type 66) violation should have been reported to SDWIS. | Y | 1/1/12 - 6/30/12 | N | 7 smpls: 16, 18, 19, 19, 20, 23, & 27 ppb | Letter dated 7/12/2012 indicates exceedance and need to repeat public notice every 12 months (with updated sample results). | not in file | Unknown | not in file | Continue to feed blended polyphosphate. | N | n/a | y | Mar-12 | N | n/a | 1/29/2014 |  | System has collected 4 rounds of samples below the AL since the AL exceedances. In 2011, the 10 triennial samples produced lead exceedance. Went to 20 samples every 6 months and exceeded again 11/29/2011.
MI0004730 | NEWBERRY CORRECTIONAL FACILITY | MI | LEAD SUMMARY | 0.038 | 38 | 2011-07-01 | 2011-12-31 | 2012-08-28 10:11 | 2018-03-01 11:05 |  | Yes | [17 empty] | Based on the responses to LCN questions, a LCN (Type 66) violation should have been entered into SDWIS. | MDEQ 7/17 - Staff were in communication with the supply and determined PE had been issued, but MDEQ failed to retain documentation, therefore no violation issued. | Based on responses to Questions 7 and 8, a LCR (Type 66) violation should have been reported to SDWIS. | Y | 10/1/11 - 12/31/11 | N | 5 smpls: 17, 24, 38, 40, & 48 ppb | 1/24/2012 letter details exceedance for the 11/29/2011 samples (20) collected. Indicates the PN Lead Ed was already completed for this 12 month period. | not in file | Have fax 3/19/2012 that the Consumer Notice of Lead Result Certification was done 2/10/2012. No sample attached of a specific result. Operator indicated the information was posted for general population and for employees. | 2/10/12 - faxed to DEQ on 3/19/12 | Continue to feed blended polyphosphate. | N | n/a | installed | Mar-12 | N | n/a | 1/29/2014 |  | Throughout this event, we had numerous emails back and forth about providing lead ed, treatment etc. but there are no copies of them in the files.
MI0004730 | NEWBERRY CORRECTIONAL FACILITY | MI | LEAD SUMMARY | 0.022 | 22 | 2009-01-01 | 2011-12-31 | 2011-11-22 16:28 | 2018-02-28 16:20 |  | Yes | [17 empty] | Based on responses to PE Questions, it appears a PE (Type 65) violation should have been entered into SDWIS. Based on the responses to LCN questions, a LCN (Type 66) violation should have been entered into SDWIS. | MDEQ 7/17 - Staff were in communication with the supply and determined PE had been issued, but MDEQ failed to retain documentation, therefore no violation issued. Lead consumer notice inadvertently omitted. | Based on responses to Questions 5 and 6, a PE (Type 65) violation should have been reported to SDWIS. Also, based on responses to Questions 7 and 8, a LCR (Type 66) violation should have been reported to SDWIS. | Y | June to Sept, 2011 | N | 3 smpls: 17, 22, & 51 ppb | Told in a 10/25/2011 letter the PN Lead ED was due by 1/1/2012. The notice was posted for general population and given to employees in Dec. 2011 but file does not document exactly when. Email was used to communicate the requirements and answer questions | not in file | Not documented. Operator was provided with the PE as part of complete reporting forms sent to him. | not in file | Study was not initiated. The facility contacted Elhorn in the fall 2011 and in March/April 2012 they began feeding a blended polyphosphate at all three well houses. | N | n/a | initiated | Mar-12 | N | n/a | In 2011, the 10 triennial samples produced lead exceedance. Went to 20 samples every 6 months and exceeded again 11/29/2011. |  | 10/12/2011 - MDEQ met with the owners/managers at the facility to discuss this latest exceedance and the need to look into treatment since this had been an ongoing problem over the years-in and out of compliance. They shortly thereafter contacted contrac
MI0005268 | PERE MARQUETTE TWP - WELLS | MI | LEAD SUMMARY | 0.019 | 19 | 2012-01-01 | 2014-12-31 | 2014-11-24 14:13 | 2018-03-26 12:54 |  | Yes | [20 empty] | Y | June to Sept, 2014 | N | 1 smpl: 26 ppb | Y | 11/29/2014 | Y | no date stamp | N | N | n/a | N/Y | n/a | Y | N | 1/1/2016 |  | Resolved
MI0005268 | PERE MARQUETTE TWP - WELLS | MI | LEAD SUMMARY | 0.016 | 16 | 2008-07-01 | 2008-12-31 | 2009-02-17 12:56 | 2018-03-26 12:54 |  | Yes | [20 empty] | Y | June to Sept, 2008 | N | 1 smpl: 30 ppb | Y? (not in file) | 11/20/2008 | N | n/a | Not a treatment study | N | n/a | N | n/a | N | N | 1/1/2010 |  | Resolved
MI0005785 | ROMULUS | MI | LEAD SUMMARY | 0.042 | 42 | 2015-01-01 | 2017-12-31 | 2017-08-31 08:25 | 2018-03-26 12:54 |  |  | Y | 2 samples - 22 ppb, 120 ppb | Y | Y | Y | Y | Y | 2. Orthophosphate | Southwest: 7.14 to 7.48 Springwells 7.05 to 7.37 | Southwest 0.86 to 1.26 ppm Springwells 0.9 to 3.42 ppm | N | Y | Y | Y |  | Immediately replaced LSL at high site | OCCT provided by seller to this community, not by the community itself. 2018-1 90th was 7 ppb. Waiting on 2nd set.
MI0006042 | SHERWOOD SHORES CONDOMINIUMS | MI | LEAD SUMMARY | 0.045 | 45 | 2018-01-01 | 2018-06-30 | 2018-05-31 11:12 | 2018-08-29 10:28 | Newly reported (after April 2018 freeze)
MI0006042 | SHERWOOD SHORES CONDOMINIUMS | MI | LEAD SUMMARY | 0.05 | 50 | 2015-01-01 | 2017-12-31 | 2017-11-29 16:23 | 2018-03-26 12:54 |  |  | Y | 1 sample - 100 ppb | Y | Y | Y | N | N | 5. None | 7.90 & 7.94 | n/a | N | N | N | N |  | Investigative sampling
MI0006110 | SOUTH LYON, CITY OF | MI | LEAD SUMMARY | 0.0155 | 15.5 | 2011-01-01 | 2013-12-31 | 2014-02-12 15:54 | 2018-03-14 14:20 |  | Yes | [20 empty] | Y | June to Sept, 2013 | N | 4 smpls: 16, 24, 36 & 37 ppb | Y | 11/26/2013 | Y | 10/10/2013 | Not a treatment study | N | n/a | N/Y | n/a | Unknown | N/A | 1/1/2015 | adjusted phosphate feed | Resolved. The district engineer consulted with the supply and asked that they review their dosage and make adjustments accordingly. System also bought new testing equipment.
MI0006232 | SPRING LAKE CLUB CONDOMINIUMS | MI | LEAD SUMMARY | 0.031 | 31 | 2014-07-01 | 2014-12-31 | 2014-11-24 14:13 | 2018-03-15 10:55 |  | Yes | [20 empty] | Y | 7/1/14 - 12/31/14 | N | 5 smpls: 23, 28, 29, 31, & 44 ppb | Y | 11/12/2014 | Y | 10/1/2014 | Not a treatment study, fixture replacement | Y | 12/14/2014 | N | n/a | Y | N | 1/1/2016 |  | Resolved. Each unit that tested >10 ppb had the fixtures replaced. Follow-up sampling was done at all 29 units.
MI0006232 | SPRING LAKE CLUB CONDOMINIUMS | MI | LEAD SUMMARY | 0.042 | 42 | 2014-01-01 | 2014-06-30 | 2014-05-30 12:43 | 2018-03-15 10:55 |  | Yes | [17 empty] | Based on responses to PE Questions, it appears a PE (Type 65) violation should have been entered into SDWIS. | MDEQ 7/17 - A violation should have been issued; however, the supply had issued PE in 11/13. Analyst may have determined additional PE not necessary since it was less than 1 year since previously issued. Analyst no longer with the program. | Based on responses to Questions 5 and 6, a PE (Type 65) violation should have been reported to SDWIS. | Y | 1/1/14 - 6/30/14 | N | 6 smpls: 19, 19, 21, 31, 42, & 46 ppb | N | not in file | Y | 4/30/2014 | N - rec'd viol | N | n/a | N | n/a | N | N | 5/31/2016 |  | System collected 2 rounds below the AL in 2016 - 5/31/16 & 9/06/16. Several violations issued following this round - WQP, LCN, PE, CCT Study, SOWT
MI0006232 | SPRING LAKE CLUB CONDOMINIUMS | MI | LEAD SUMMARY | 0.018 | 18 | 2010-01-01 | 2012-12-31 | 2014-02-12 15:54 | 2018-03-15 10:55 |  | Yes | [20 empty] | N - Entered into wrong compl period.
MI0006575 | SUGARTREE APARTMENTS | MI | LEAD SUMMARY | 0.151 | 151 | 2011-01-01 | 2013-12-31 | 2015-03-26 10:22 | 2018-03-20 11:53 |  | Yes | [17 empty] | Based on responses to PE Questions, it appears a PE (Type 65) violation should have been entered into SDWIS. Based on the responses to LCN questions, a LCN (Type 66) violation should have been entered into SDWIS. | MDEQ 7/17 - Staff was in communication with WS by phone or email before AL letter was sent, evident by submission of letter stating they would try to meet AL through sampling. PE not in file. Staff no longer with program, unable to determine if PE was p | Based on responses to Questions 5 and 6, a PE (Type 65) violation should have been reported to SDWIS. Also, based on responses to Questions 7 and 8, a LCR (Type 66) violation should have been reported to SDWIS. | Y | June to Sept, 2013 | N | 4 smpls: 27, 43, 73, & 28 ppb | N |  | late | 1/29/2014 | Not a treatment study | N | n/a | N/Y | n/a | N | n/a | 8/9/2016 |  | System collected 2 rounds below the AL in 2016 - 1/12/16 & 8/9/16. Both were collected properly and below the AL. System has RTC. System was initially considered resolved after 2 6 month rounds in 2014. Further investigation found that some of the samp
MI0006705 | UAW FAMILY EDUCATION CENTER | MI | LEAD SUMMARY | 0.117 | 117 | 2013-01-01 | 2015-12-31 | 2015-11-27 13:40 | 2018-03-20 11:53 |  | Yes | [20 empty] | Y | June to Sept, 2015 | N | 8 smpls: 18, 18, 54, 61, 71, 76, 117 & 430 ppb | Y | 10/2/2015 | Y | 9/10/2015 | Y | complete | 3/30/2016 | installing treatment | not complete | N | n/a | 1/19/2016 |  | Supply converted to non-community system in Nov 2016. WSSN MI0020479-16. 2 rounds under; however still requiring Installation of orthophosphate treatment due to recurrence.
MI0006705 | UAW FAMILY EDUCATION CENTER | MI | LEAD SUMMARY | 0.0452 | 45.2 | 2010-01-01 | 2012-12-31 | 2012-11-30 09:26 | 2018-03-01 11:05 |  | Yes | [20 empty] | Y | June to Sept, 2012 | N | 5 smpls: 18, 19, 21, 45, & 46 ppb | Y | 11/19/2012 | Y | 10/8/2012 | Not a treatment study | N | n/a | N | n/a | N |  | 1/1/2014
MI0006792 | V F W NATIONAL HOME | MI | LEAD SUMMARY | 0.024 | 24 | 2015-01-01 | 2017-12-31 | 2017-08-31 08:25 | 2018-03-26 12:54 |  |  | Y | 2 samples - 17 ppb and 36 ppb | Y | Y | Y | N | N | 2. Orthophosphate | 7.36 & 7.38 | 0.35 to 3.3 ppm | N | N | N | N |  | Cleaned dirty injection ports which were giving inconsistent feed rates; increased feed rates | 2018-1 90th is 10 ppb. Waiting on 2nd set.
MI0040028 | VILLAGE EAST ESTATES | MI | LEAD SUMMARY | 0.097 | 97 | 2015-01-01 | 2017-12-31 | 2017-11-29 16:23 | 2018-03-26 12:54 |  |  | Y | 1 sample - 190 ppb | Y | Y | N | N | N | 5. None | 7.95 & 8.03 | n/a | N | N | N | N |  |  | 2018-1 90th is 2 ppb. Waiting on 2nd set.
MI0040090 | TWIN PINES MOBILE HOME PARK | MI | LEAD SUMMARY | 0.016 | 16 | 2013-01-01 | 2015-12-31 | 2015-12-17 16:14 | 2018-03-20 11:53 |  | Yes | [20 empty] | Y | June to Sept, 2015 | Yes, 5th sample (0 ppb) due to hold time | 1 smpl: 16 ppb | done by state appointed deadline | 12/31/2015 | Y | 12/31/2015 | Y | N | 4/11/2016 (late) | Not installed/ WQP yes | n/a | No | n/a | 9/25/2016 |  | Supply collected 2 rounds in 2016, 6/29 and 9/25. Both were below the AL.
MI0040217 | MAPLEVIEW ESTATES | MI | LEAD SUMMARY | 0.017 | 17 | 2012-01-01 | 2014-12-31 | 2014-11-24 14:13 | 2018-03-15 10:55 |  | Yes | [20 empty] | Y | June to Sept, 2014 | N | 1 smpl: 31 ppb | Y | 11/25/2014 | Y | 10/8/2014 | Y | N | 2/26/2015 | N |  | Y | N | 1/1/2016 |  | Resolved
MI0040223 | ARBOR VILLAGE | MI | LEAD SUMMARY | 0.049 | 49 | 2017-07-01 | 2017-12-31 | 2017-11-29 16:23 | 2018-03-26 12:54 |  |  | Y | 4 samples - 46 ppb, 49 ppb, 51 ppb, 56 ppb | Y | Y | Y | N | N | 4. Other | 7.2 to 7.3 | 0.5 to 3.5 ppm | N | N | N | N |  | Installed another injection port; switched to higher orthophosphate blend | 2018-1 90th is 1 ppb. Waiting on 2nd set.
MI0040223 | ARBOR VILLAGE | MI | LEAD SUMMARY | 0.016 | 16 | 2015-01-01 | 2017-12-31 | 2016-12-02 14:11 | 2018-03-22 13:44 |  | No | Y | 2 samples - 16 ppb, 32 ppb | Y | Y | Y | N | N | 5. None | 7.2 to 7.3 | n/a | N | N | N | N |  | Corrected well house/injection issues; resumed feeding blended phosphate
MI0040319 | ALAN'S PARK - FOWLERVILLE | MI | LEAD SUMMARY | 0.04 | 40 | 2013-01-01 | 2015-12-31 | 2015-11-27 13:40 | 2018-03-20 11:53 |  | Yes | [20 empty] | Y | June to Sept, 2015 | N | 1 smpl: 68 ppb | Y | 11/17/2015 | Y | 11/17/2015 | Y | pending - past due | due 3/31/16 | N/Y | n/a | UNK. | N/A | 5/15/2016 |  | System collected 2nd round of 6 mth sampling on 5/15/16, which was also below the AL. System currently has 1 round under the AL. Second 6 month round due by 6/30/16.
MI0040335 | HOLIDAY VILLAGE MOBILE HOME PARK | MI | LEAD SUMMARY | 0.016 | 16 | 2015-01-01 | 2017-12-31 | 2017-11-29 16:23 | 2018-03-26 12:54 |  |  | Y | 1 sample - 28 ppb | Y | Y | Y | N | N | 5. None | 7.76 | n/a | N | N | Y | N |  | Replaced plumbing at high site | 2018-1 90th is 5 ppb. Waiting on 2nd set.
MI0040438 | FREELAND MOBILE HOME PARK | MI | LEAD SUMMARY | 0.017 | 17 | 2015-01-01 | 2017-12-31 | 2017-11-29 16:23 | 2018-03-26 12:54 |  |  | Y | 2 samples - 17 ppb, 33 ppb | Y | Y | N | N | N | 4. Other | 7.80 & 7.81 | 0.2 to 1.28 ppm | N | N | N | N |  |  | 2018-1 90th is 1 ppb. Waiting on 2nd set.
MI0060425 | THORNAPPLE MANOR | MI | LEAD SUMMARY | 0.031 | 31 | 2015-01-01 | 2017-12-31 | 2017-08-31 08:25 | 2018-03-26 12:54 |  | No | Y | 6 samples - 18 ppb, 19 ppb, 24 ppb, 26 ppb, 36 ppb, and 302 ppb | Y | Y | Y | N | N | 5. None | 7.4 | n/a | Y | N | N | N |  | Installed softener bypass and mixing valve
MI0062841 | MEDILODGE OF STERLING | MI | LEAD SUMMARY | 0.074 | 74 | 2014-01-01 | 2016-12-31 | 2016-12-02 14:11 | 2018-03-26 12:54 |  | Yes
MI0220075 | AUTRAIN-ONOTA PUBLIC SCHOOL | MI | LEAD SUMMARY | 0.019 | 19 | 2008-07-01 | 2008-12-31 | 2009-03-02 11:50 | 2013-06-06 10:44 |  | Yes | [18 empty] | MDEQ 7/2017: 2013 was first year of this requirement in Michigan for this system. Posted LCN 1/31/14. NCWS Program has no means of reporting Type 65 and 66 violations to SDWIS. | Based on responses to Questions 7 and 8, a LCR (Type 66) violation should have been reported to SDWIS. November 2017 R5 follow-up correction: Disregard this question because the first standard and reduced Lead and Copper monitoring periods that the LCN r | Y | Aug-08 | N | 19 | Y | 11/24/2008 | N |  | N | N |  | N |  | N |  | 1/1/2009 |  | Requires more investigation
MI0320360 | EAST MARTIN CHRISTIAN SCHOOL | MI | LEAD SUMMARY | 0.0167 | 16.7 | 2010-07-01 | 2010-12-31 | 2010-12-10 08:51 | 2017-12-07 16:42 |  | Yes | [18 empty] | MDEQ 7/2017: 2013 was first year of this requirement in Michigan for this system. Posted LCN 8/1/13. NCWS Program has no means of reporting Type 65 and 66 violations to SDWIS. | Based on responses to Questions 7 and 8, a LCR (Type 66) violation should have been reported to SDWIS. November 2017 R5 follow-up correction: Disregard this question because the first standard and reduced Lead and Copper monitoring periods that the LCN r | Y | Sep-10 | N | 69, 18 | Y | 4/18/2011 | N |  | N | N |  | N |  | Y |  | 1/1/2013 |  | Resolved
MI0320571 | KRUGER COMMODITIES | MI | LEAD SUMMARY | 0.022 | 22 | 2016-07-01 | 2016-12-31 | 2017-05-31 10:02 | 2018-03-09 12:47 |  | No | Y | 2 out of 10. 22ppb and 94ppb from same location | Y | Y | Y | N | N | 5. None |  | NA | Y | Y | Y |  |  | material replacement and resampling | Sample siting plan was not correct prior to ALE. Site visit completed 10/25/2017. Compliance monitoring to begin January 2018.
MI0320600 | B&G CUSTOM WORKS,INC. | MI | LEAD SUMMARY | 0.0166 | 16.6 | 2017-01-01 | 2017-06-30 | 2017-05-31 10:02 | 2018-03-09 12:47 |  | No | Y | 1 of 5 31ppb | Y | Y |  | N | N | 5. None |  | NA | Y | Y | Y |  |  | removed offending sink | Sample siting plan was not correct prior to ALE. Site visit completed 10/25/2017. Compliance monitoring to begin January 2018. First round all ND
MI1320024 | DORIS KLAUSSEN DEV CENTER | MI | LEAD SUMMARY | 0.155 | 155 | 2012-07-01 | 2012-12-31 | 2013-06-06 10:44 | 2017-12-07 16:42 |  | Yes | [17 empty] | Based on responses to PE Questions, it appears a PE (Type 65) violation should have been entered into SDWIS. Based on the responses to LCN questions, a LCN (Type 66) violation should have been entered into SDWIS. | MDEQ 7/2017: 2013 was first year of this requirement in Michigan for this system. Posted LCN 8/2/13. NCWS Program has no means of reporting Type 65 and 66 violations to SDWIS. | Based on responses to Questions 5 and 6, a PE (Type 65) violation should have been reported to SDWIS. Also, based on responses to Questions 7 and 8, a LCR (Type 66) violation should have been reported to SDWIS. | Y | Oct-12 | N | 299 | N |  | N |  | N | N |  | N |  | N |  | 1/1/2014 |  | Resolved
MI1320042 | PURDY SCHOOL | MI | LEAD SUMMARY | 0.059 | 59 | 2014-07-01 | 2014-12-31 | 2016-03-08 12:23 | 2018-03-09 12:47 |  | Yes
MI1420041 | KINCHELOE ELEMENTARY SCHOOL | MI | LEAD SUMMARY | 0.016 | 16 | 2010-07-01 | 2010-12-31 | 2011-12-01 06:53 | 2016-09-28 21:39 |  | Yes | [18 empty] | MDEQ 7/2017: 2013 was first year of this requirement in Michigan for this system. Posted LCN 9/21/15. NCWS Program has no means of reporting Type 65 and 66 violations to SDWIS. | Based on responses to Questions 7 and 8, a LCR (Type 66) violation should have been reported to SDWIS. November 2017 R5 follow-up correction: Disregard this question because the first standard and reduced Lead and Copper monitoring periods that the LCN re | Y | Nov-10 | N | 19 | Y | 2/7/2011 | N |  | N | N |  | N |  | N |  | 1/1/2013 |  | Resolved
MI1620082 | CHEBOYGAN AREA SCHOOLS ADMIN. BLDG. | MI | LEAD SUMMARY | 0.017 | 17 | 2013-01-01 | 2013-06-30 | 2013-09-03 11:15 | 2017-12-07 16:42 |  | Yes | [17 empty] | Based on responses to PE Questions, it appears a PE (Type 65) violation should have been entered into SDWIS. | MDEQ 7/2017: Posted LCN 9/12/13. NCWS Program has no means of reporting Type 65 and 66 violations to SDWIS. | Based on responses to Questions 5 and 6, a PE (Type 65) violation should have been reported to SDWIS. Also, based on responses to Questions 7 and 8, a LCR (Type 66) violation should have been reported to SDWIS. | Y | Jun-13 | N | 31 | N |  | Y | 9/12/2013 | N | N |  | N |  | Y |  | 1/1/2015 |  | Resolved
MI1820020 | CLARE-GLADWIN RESD | MI | LEAD SUMMARY | 0.0172 | 17.2 | 2017-07-01 | 2017-12-31 | 2018-03-09 12:47 |  |  |  | Y | 6 samples - 15 ppb, 15 ppb, 17 ppb, 19 ppb, 20 ppb, 30 ppb | Y | Y | Y | N | N | 5. None | Unknown | NA | N | Y |  |  | Supply has completed 1st round of semiannual MR, below AL | Bottled water, removed fixtures from use | New well installed 6/7/2017 prior to sampling in 9/2017.
MI1820290 | Farwell Alternative Education | MI | LEAD SUMMARY | 0.02 | 20 | 2013-01-01 | 2013-06-30 | 2013-11-27 10:42 | 2017-12-07 16:42 |  | Yes | [17 empty] | Based on responses to PE Questions, it appears a PE (Type 65) violation should have been entered into SDWIS. | MDEQ 7/2017: NCWS Program has no means of reporting Type 65 and 66 violations to SDWIS. | Based on responses to Questions 5 and 6, a PE (Type 65) violation should have been reported to SDWIS. | Y | Jun-13 | N | 20 | N | 6/15/2016 | Y | 9/26/2013 | N | N |  | N |  | N |  | 1/1/2015 |  | Resolved
MI1920059 | RILEY ELEMENTARY SCHOOL | MI | LEAD SUMMARY | 0.0238 | 23.8 | 2011-07-01 | 2011-12-31 | 2013-06-06 10:44 | 2016-09-28 21:39 |  | Yes | [17 empty] | Based on responses to PE Questions, it appears a PE (Type 65) violation should have been entered into SDWIS. Based on the responses to LCN questions, a LCN (Type 66) violation should have been entered into SDWIS. | MDEQ 7/2017: 2013 was first year of this requirement in Michigan for this system. Posted LCN 7/18/13. NCWS Program has no means of reporting Type 65 and 66 violations to SDWIS. | Based on responses to Questions 5 and 6, a PE (Type 65) violation should have been reported to SDWIS. Also, based on responses to Questions 7 and 8, a LCR (Type 66) violation should have been reported to SDWIS. | Y | Dec-11 | N | 37, 26 | Y | 5/4/2012 | N |  | N | N |  | N |  | Y |  | 1/1/2014 | Rmvd dead end piping and installed insulation on pipes in boiler room | Requires more investigation
MI2220079 | Verso Corporation | MI | LEAD SUMMARY | 0.0242 | 24.2 | 2016-07-01 | 2016-12-31 | 2017-09-08 07:55 | 2018-03-09 12:47 |  | Yes
MI2320093 | DIMONDALE ELEMENTARY SCHOOL | MI | LEAD SUMMARY | 0.0228 | 22.8 | 2015-07-01 | 2015-12-31 | 2015-11-25 08:33 | 2018-03-09 12:47 |  | Yes | [20 empty] | Y | Aug-15 | N | 31, 26 | Y | 8/25/2015 | Y | 10/20/2015 | N | N |  | N |  | Y |  | 7/1/2016 | Adjst softener | Two consecutive 6-month rounds of compliance sampling completed 12/19/2016. Results well below 15 ppb. System returned to compliance in January 2017.
MI2320294 | POLLY PRODUCTS ALR, LLC | MI | LEAD SUMMARY | 0.0196 | 19.6 | 2016-07-01 | 2016-12-31 | 2017-03-02 17:22 | 2018-03-09 12:47 |  | Yes | [20 empty] | Y | 16-Oct | N | 1 sample, 28 | Y | 11/29/2016 | Y | 12/22/2016 | N | N |  | N |  | Y | N |  |  | Supply replaced and resampled fixture immediately after ALE was triggered. Pb levels dropped after new fixture installed. Completed first round of semiannual sampling.
MI2520452 | DIECK ELEMENTARY | MI | LEAD SUMMARY | 0.0275 | 27.5 | 2017-07-01 | 2017-12-31 | 2017-12-07 16:42 | 2018-03-09 12:47 |  |  | Y | 1 of 5 43 ppb | Y | Y | Y | N | N | 5. None | Unknown | NA | N | Y | Y |  | Supply has completed 1st round of semiannual MR | Fiixture replacement of elevated taps
MI2820036 | FIFE LAKE ELEMENTARY SCHOOL | MI | LEAD SUMMARY | 0.022 | 22 | 2016-07-01 | 2016-12-31 | 2017-03-02 17:22 | 2018-03-09 12:47 |  | Yes | [20 empty] | Y | Mar-17 | N | 2 samples 28 & 16 | Unknown | 10/30/2017 | Y | 2/27/2017 | N | N |  |  |  | Y |  |  |  | School is working on plan for materail replacement.
MI2920616 | Good Shepherd Church | MI | LEAD SUMMARY | 0.046 | 46 | 2008-01-01 | 2008-06-30 | 2008-09-02 12:00 | 2013-06-06 10:44 |  | Yes | [20 empty] | Y | Jun-08 | N | 79 | Y | 7/16/2008 | N |  | N | N |  | N |  | N |  | 7/1/2009 |  | Resolved
MI3020031 | NORTH ADAMS PUBLIC SCHOOLS | MI | LEAD SUMMARY | 0.04 | 40 | 2011-01-01 | 2011-06-30 | 2011-06-03 10:10 | 2017-12-07 16:42 |  | Yes | [17 empty] | Based on the responses to LCN questions, a LCN (Type 66) violation should have been entered into SDWIS. | MDEQ 7/2017: 2013 was first year of this requirement in Michigan for this system. Posted LCN 2/12/15. NCWS Program has no means of reporting Type 65 and 66 violations to SDWIS. | Based on responses to Questions 7 and 8, a LCR (Type 66) violation should have been reported to SDWIS. | Y | Mar-11 | N | 80 | Y | 3/15/2011 | N |  | N | N |  | N |  | Y |  | 1/1/2014 |  | Resolved
MI3320169 | VLAHAKIS MANAGEMENT COMPANY | MI | LEAD SUMMARY | 0.0749 | 74.9 | 2013-01-01 | 2013-06-30 | 2013-11-27 10:42 | 2018-03-09 12:47 |  | Yes | [20 empty] | Y | Feb-13 | N | 83, 56, 19 | Y | 3/18/2013; 8/4/2016 | Y | 8/15/2013; 7/18/2016 | Y | Y |  | Y | 5/23/16 | Y | N | 7/1/2016 |  | Still investigating. Waiting for 1st successful round of testing by Dec 31, 2016.
MI3320180 | Colt's and Filly's Childcare | MI | LEAD SUMMARY | 0.0218 | 21.8 | 2014-01-01 | 2014-06-30 | 2014-06-02 14:14 | 2018-03-09 12:47 |  | Yes | [20 empty] | Y | Feb-14 | N | 69 | Y | 2/10/2014 | Y | 3/25/2014 | N | N |  | N |  | N |  | 1/1/2016 |  | Resolved
MI3420086 | EIGHT CAP IONIA CO. OUTREACH | MI | LEAD SUMMARY | 0.017 | 17 | 2015-07-01 | 2015-12-31 | 2016-03-08 12:23 | 2018-03-09 12:47 |  | Yes
MI3420086 | EIGHT CAP IONIA CO. OUTREACH | MI | LEAD SUMMARY | 0.016 | 16 | 2017-07-01 | 2017-12-31 | 2017-12-07 16:42 | 2018-03-09 12:47 |  |  | Y |  | Y | Y | Y | UNKNOWN | UNKNOWN | 5. None |  |  | N | N | Y | N | Supply has completed 1st round of semiannual sampling with results in compliance. Tap with ALE was removed and not replaced. They now only have 2 drinking water fixtures. SER | [5 empty] | Y | Jul-15 | N | 25 | Y | 8/21/2015 | Y | 12/15/2015 | N | N |  | N |  | N |  | 1/1/2016 |  | Resolved
MI3420231 | FAITH COMMUNITY CHRISTIAN SCH. | MI | LEAD SUMMARY | 0.017 | 17 | 2015-01-01 | 2015-06-30 | 2015-11-25 08:33 | 2018-03-09 12:47 |  | Yes | [20 empty] | Y | Jun-15 | N | 17 | Y | 7/22/2015 | Y | 11/16/2015 | N | N |  | N |  | Y |  | 7/1/2015 |  | 2nd round of sampling completed. Both rounds below AL.
MI3920018 | Lakeland Reformed Church | MI | LEAD SUMMARY | 0.0155 | 15.5 | 2010-01-01 | 2010-06-30 | 2010-12-10 08:51 | 2016-09-28 21:39 |  | Yes | [18 empty] | MDEQ 7/2017: 2013 was first year of this requirement in Michigan for this system. Posted LCN 12/8/14. NCWS Program has no means of reporting Type 65 and 66 violations to SDWIS. | Based on responses to Questions 5 and 6, a PE (Type 65) violation should have been reported to SDWIS. Also, based on responses to Questions 7 and 8, a LCR (Type 66) violation should have been reported to SDWIS. November 2017 R5 follow-up correction: Dis | Y | Apr-10 | N | 26 | N |  | N |  | N | N |  | N |  | Y |  | 1/1/2012 |  | Resolved
MI4120203 | WHITE EARLY CHILDHOOD CENTER | MI | LEAD SUMMARY | 0.0906 | 90.6 | 2017-07-01 | 2017-12-31 | 2017-12-07 16:42 | 2018-03-09 12:47 |  |  | Y |  | Y | Y | Y | UNKNOWN | UNKNOWN | 5. None |  |  | N | N | Y | N | Supply has completed 1st round of semiannual sampling with results in compliance. All taps were replaced with lead-free fixtures. SER |  | Grounding issue was discovered and corrected.
MI4120793 | MAGNA MIRRORS | MI | LEAD SUMMARY | 0.02 | 20 | 2013-07-01 | 2013-12-31 | 2013-11-27 10:42 | 2018-03-09 12:47 |  | Yes | [20 empty] | Y | Sep-13 | N | 17, 34, 20 | Y | 9/13/2013 | Y | 9/13/2013 | N | N |  | N |  | Y |  | 1/1/2015 |  | Resolved
MI4120810 | MAST YOUNG PLANTS | MI | LEAD SUMMARY | 0.017 | 17 | 2015-07-01 | 2015-12-31 | 2017-03-02 17:22 | 2018-03-09 12:47 |  | Yes
MI4121001 | SPEEDRACK MIDWEST | MI | LEAD SUMMARY | 0.062 | 62 | 2017-01-01 | 2017-06-30 | 2017-09-08 07:55 | 2018-03-09 12:47 |  | No | Y |  | Y | Y | Y | UNKNOWN | UNKNOWN | 5. None |  |  | N | N | Y | N | Supply has replaced and removed fixtures to address ALE. Well was recently replaced, will see if that affects lead levels. SER
MI4520028 | BLUEBIRD RESTAURANT & BAR | MI | LEAD SUMMARY | 0.0325 | 32.5 | 2014-07-01 | 2014-12-31 | 2015-03-03 10:40 | 2018-03-09 12:47 |  | Yes | [17 empty] | Based on responses to PE Questions, it appears a PE (Type 65) violation should have been entered into SDWIS. Based on the responses to LCN questions, a LCN (Type 66) violation should have been entered into SDWIS. | MDEQ 7/2017: 2016 was first year of this requirement. Posted LCN 3/16/2016. NCWS Program has no means of reporting Type 65 and 66 violations to SDWIS. | Based on responses to Questions 5 and 6, a PE (Type 65) violation should have been reported to SDWIS. Also, based on responses to Questions 7 and 8, a LCR (Type 66) violation should have been reported to SDWIS. | Y | Dec-14 | N | 65 | N |  | N |  | N | N |  | N |  | Y |  | 7/1/2015 |  | DEQ waiting for evidence of 2nd round sampling to have been completed by end of 2016.
MI4720157 | PINCKNEY SCHOOLS - PATHFINDER SCHOOL | MI | LEAD SUMMARY | 0.018 | 18 | 2016-07-01 | 2016-12-31 | 2017-03-02 17:22 | 2018-03-09 12:47 |  | Yes | [20 empty] | Y | Sep.-16 | N | 1, | N | 12/5/2016 | Y | 11/8/2016 | N | N |  | N |  | Y |  |  |  | Offending fixture replaced. Pending second round of compliance samples. First round of 17 samples below 90th percentil.
MI4720357 | PINCKNEY SCHOOLS - COUNTRY ELEMENTARY | MI | LEAD SUMMARY | 0.016 | 16 | 2008-07-01 | 2008-12-31 | 2009-03-02 11:50 | 2013-09-03 11:15 |  | Yes | [18 empty] | MDEQ 7/2017: 2013 was first year of this requirement. Posted LCN 2/25/14 |  | Y | Dec-08 | N | 32 | Y | 2/19/2009 | N |  | N | N |  | N |  | N |  | 1/1/2010 |  | Resolved
MI4720763 | THE RE/MAX BUILDING | MI | LEAD SUMMARY | 0.062 | 62 | 2016-07-01 | 2016-12-31 | 2017-03-02 17:22 | 2018-03-09 12:47 |  | Yes | [20 empty] | Y | Sep.-16 | N | 1, 120 | N | 12/10/2016 | Y | 11/15/2016 | N | N |  | N |  | N |  |  |  | Pending second round of semi annual sampling.
MI5220042 | Silver Creek Church | MI | LEAD SUMMARY | 0.0315 | 31.5 | 2016-07-01 | 2016-12-31 | 2016-12-14 08:34 | 2018-03-09 12:47 |  | No | Y | 2 - 41 ppb and 23 ppb | Y | Y | Y | UNKNOWN | UNKNOWN | 5. None | Unknown |  | N |  | N | N | Supply has completed multiple rounds of semi annual | fixture replacement, aerator cleaning |  |  |  |  | Y | Jul-16 | N | 2, (40, 23) | Y | 8/29/2016 | Y | 8/23/2016 | N | N |  | N |  | Y |  |  | well replacement due to lead packer. | Source sample indicated elevated lead - lead packer thought to be the issue. Some fixtures replaced but samples still exceed ALE.
MI5220072 | Tilden Pit Service Building (old Empire) | MI | LEAD SUMMARY | 0.1375 | 137.5 | 2016-07-01 | 2016-12-31 | 2016-12-14 08:34 | 2018-03-09 12:47 |  | No | Y | 2- 55 ppb and 220 ppb | Y | Y | Y | UNKNOWN | UNKNOWN | 5. None | Unknown |  | N |  | Y | N | Supply has completed multiple rounds of semi annual | fixture replacement |  |  | MDEQ 7/2017: Posted LCN 6/16/17 |  | Y | Jul-16 | N | 2, (220, 55) | Y | 8/23/2016 | N |  | N | N |  | N |  | Y |  |  |  | Some fixtures replaced but samples still exceed ALE.
MI5220151 | Reinhart Instutional Foods | MI | LEAD SUMMARY | 0.0288 | 28.8 | 2016-07-01 | 2016-12-31 | 2016-12-14 08:34 | 2018-03-09 12:47 |  | Yes | [20 empty] | Y | Jul-16 | N | 1, (55) | Y | 8/8/2016 | Y | 9/20/2016 | N | N |  | N |  | Y |  | 9/27/2016 |  | Resolved
MI5420195 | MORLEY ELEMENTARY | MI | LEAD SUMMARY | 0.045 | 45 | 2006-01-01 | 2006-06-30 | 2007-05-21 13:00 | 2010-08-30 10:38 |  | Yes | [20 empty] | Y | Feb-06 | N | 45 | Y | 12/18/2006 | N |  | N | N |  | N |  | N |  | 7/1/2007 |  | Resolved
MI5420437 | US MARBLE | MI | LEAD SUMMARY | 0.0286 | 28.6 | 2015-07-01 | 2015-12-31 | 2016-03-08 12:23 | 2018-03-09 12:47 |  | Yes
MI5720056 | FALMOUTH PRESCHOOL | MI | LEAD SUMMARY | 0.1115 | 111.5 | 2016-07-01 | 2016-12-31 | 2017-05-31 10:02 | 2018-03-09 12:47 |  | No | Y | 1-21 ppb | Y | Y | Y | N | N | 5. None | Unknown | NA | N | Y | Y |  | Pending | Posted taps, provided bottled water
MI5820156 | WHITEFORD HIGH SCHOOL | MI | LEAD SUMMARY | 0.026 | 26 | 2014-07-01 | 2014-12-31 | 2016-12-14 08:34 | 2018-03-09 12:47 |  | Yes
MI5820388 | BIG DADDY'S TRUCK STOP | MI | LEAD SUMMARY | 0.0161 | 16.1 | 2014-01-01 | 2014-06-30 | 2014-08-26 17:19 | 2018-03-09 12:47 |  | Yes | [17 empty] | Based on responses to PE Questions, it appears a PE (Type 65) violation should have been entered into SDWIS. Based on the responses to LCN questions, a LCN (Type 66) violation should have been entered into SDWIS. | MDEQ 7/2017: 2016 was first year of this requirement. Posted LCN 11/30/16. NCWS Program has no means of reporting Type 65 and 66 violations to SDWIS. | Based on responses to Questions 5 and 6, a PE (Type 65) violation should have been reported to SDWIS. Also, based on responses to Questions 7 and 8, a LCR (Type 66) violation should have been reported to SDWIS. | Y | Jun-14 | N | 23 | N | 8/1/2016 | N |  | N | N |  | N |  | Y |  | 1/1/2015 |  | Resolved
MI5920043 | VESTABURG HIGH SCHOOL | MI | LEAD SUMMARY | 0.0192 | 19.2 | 2010-07-01 | 2010-12-31 | 2011-06-03 10:10 | 2017-12-07 16:42 |  | Yes | [20 empty] | Y | Dec-10 | Improper sample location | 26 | Y | 1/31/2011 | N |  | N | N |  | N |  | N |  | 1/1/2013 |  | Resolved
MI6020023 | LEWISTON K-6 SCHOOL | MI | LEAD SUMMARY | 0.021 | 21 | 2013-01-01 | 2013-06-30 | 2013-09-03 11:15 | 2017-12-07 16:42 |  | Yes | [17 empty] | Based on responses to PE Questions, it appears a PE (Type 65) violation should have been entered into SDWIS. Based on the responses to LCN questions, a LCN (Type 66) violation should have been entered into SDWIS. | MDEQ 7/2017: NCWS Program has no means of reporting Type 65 and 66 violations to SDWIS. | Based on responses to Questions 5 and 6, a PE (Type 65) violation should have been reported to SDWIS. Also, based on responses to Questions 7 and 8, a LCR (Type 66) violation should have been reported to SDWIS. | Y | Apr-13 | Improper sample location | 21, 20 | N |  | N | 9/11/2013 | N | N |  | N |  | Y |  | 1/1/2014 |  | Resolved
MI6220059 | NEWAYGO CHILD DEVELOPMENT CENTER | MI | LEAD SUMMARY | 0.03 | 30 | 2016-07-01 | 2016-12-31 | 2017-12-07 16:42 | 2018-03-09 12:47 |  |  | Y | 43130 | Y | Y | Y | N | N | 5. None | Unknown | NA | N | Y | Y |  | Pending | Posted taps, provided bottled water
MI6320778 | BAILEY LAKE ELEM SCHOOL/CCS | MI | LEAD SUMMARY | 0.017 | 17 | 2016-07-01 | 2016-12-31 | 2016-12-14 08:34 | 2018-03-09 12:47 |  | Yes | [20 empty] | y | 16-Sep | N | 17,49 | Y | 9/29/2016 | Y | 10/27/2016 | Y | N | 10/13/2016 | N | na | Y | na | 1/30/2017 | BW provided until clearance samples received | System on semi-annual monitoring. Cannot SOX ALE until one year of semi-annual monitoring completed.
MI6320790 | OAKLAND SCHOOLS-TECHNICAL CAMPUS NW | MI | LEAD SUMMARY | 0.0174 | 17.4 | 2008-07-01 | 2008-12-31 | 2009-03-02 11:50 | 2013-06-06 10:44 |  | Yes | [20 empty] | Y | Dec-08 | N | 37, 19 | Y | 1/8/2009 | N |  | N | N |  | N |  | Unknwn |  | 7/1/2009 | Fixtures were replaced and retested. | Resolved
MI6320792 | ANDERSONVILLE ELEM/CCS | MI | LEAD SUMMARY | 0.0296 | 29.6 | 2014-01-01 | 2014-06-30 | 2014-08-26 17:19 | 2018-03-09 12:47 |  | Yes | [17 empty] | Based on the responses to LCN questions, a LCN (Type 66) violation should have been entered into SDWIS. | MDEQ 7/2017: NCWS Program has no means of reporting Type 65 and 66 violations to SDWIS. | Based on responses to Questions 7 and 8, a LCR (Type 66) violation should have been reported to SDWIS. | Y | Jun-14 | N | 24, 75 | Y | 7/9/2014 | Y | 10/16/2014 | N | N |  | N |  | Unknwn |  | 7/1/2015 |  | Resolved
MI6320797 | AUTOMATION & MODULAR COMPONENTS | MI | LEAD SUMMARY | 0.046 | 46 | 2016-07-01 | 2016-12-31 | 2017-05-31 10:02 | 2018-03-09 12:47 |  | No | Y | 2 - 19 ppb and 46 ppb. Same fixture. | y | y | yes - fixture and associated plumbing replaced. | unknown | unknown | 5. None | 7.86 | NA | N | N | Y |  | 43283 | Fixture taken out of use until satisfactory samples were received after replacement.
MI6321388 | EPIC LIFE CHURCH | MI | LEAD SUMMARY | 0.039 | 39 | 2016-07-01 | 2016-12-31 | 2017-05-31 10:02 | 2018-03-09 12:47 |  | Yes
MI6322144 | SPRINGFIELD PLAINS ELEMENTARY | MI | LEAD SUMMARY | 0.031 | 31 | 2016-07-01 | 2016-12-31 | 2016-12-14 08:34 | 2018-03-09 12:47 |  | Yes | [20 empty] | Y | 16-Sep | N | 17,18,19,19,20,31,46 | Y | 9/29/2016 | Y | 10/27/2016 | Y | N | 10/13/2016 | N | na | Y | na | 1/30/2017 | BW provided until clearance samples received | System on semi-annual monitoring. Cannot SOX ALE until one year of semi-annual monitoring completed.
MI6322603 | GANEINU DAY SCHOOL | MI | LEAD SUMMARY | 0.0187 | 18.7 | 2016-07-01 | 2016-12-31 | 2016-12-14 08:34 | 2018-03-09 12:47 |  | Yes | [20 empty] | Y | 16-Sep | N | 25 | Y | 10/5/2016 | Y | 10/4/2016 | Y | N | 12/27/2016 | N | na | Y | na | 2/2/2017 | BW provided until clearance samples received | System on semi-annual monitoring. Cannot SOX ALE until one year of semi-annual monitoring completed.
MI6520157 | OGEMAW HEIGHTS HIGH SCHOOL | MI | LEAD SUMMARY | 0.017 | 17 | 2013-07-01 | 2013-12-31 | 2014-06-02 14:14 | 2018-03-09 12:47 |  | Yes | [17 empty] | Based on responses to PE Questions, it appears a PE (Type 65) violation should have been entered into SDWIS. | MDEQ 7/2017: NCWS Program has no means of reporting Type 65 and 66 violations to SDWIS. | Based on responses to Questions 5 and 6, a PE (Type 65) violation should have been reported to SDWIS. | Y | Sep-13 | N | 31, 17 | Y | 4/24/2014 | Y | 9/19/2013 | N | N |  | N |  | N |  | 1/1/2015 |  | Resolved
MI6720085 | NARTRON CORP. | MI | LEAD SUMMARY | 0.021 | 21 | 2016-07-01 | 2016-12-31 | 2016-12-14 08:34 | 2018-03-09 12:47 |  | No | Y | 1-21 ppb | Y | Y | Y | N | N | 5. None | Unknown | NA | N | Y | N |  | Pending | Pending |  |  |  |  | Y | Sep.-16 | N | 1, 21 | Y | 10/12/2016 | Y | 12/16/2016 | N | N |  |  |  | Unknown |  |  |  | Site visit scheduled. Owner indicated that they have no drinking water locations. Exceeding value collected at a hand washing station.
MI7020398 | CONSUMERS ENERGY WELLS 4,6, & 17 | MI | LEAD SUMMARY | 0.018 | 18 | 2016-07-01 | 2016-12-31 | 2017-03-02 17:22 | 2018-03-09 12:47 |  | No | Y |  | Y | Y | Y | N | N | 5. None | 7.35-7.89 | NA | Y | Y | Y |  |  | Sampled all dw locations. Replaced fixtures. Now evaluating added CCT. |  |  | WS is still in the investigation phase. Samples were collected 2/14/2017. Fixtures were replaced. Samples collected 5/1/2017. WQP on the two wells is very different. WS wants to continue to investigate and "find and fix". They may have to move toward corr |  | Y | 2016 | N | 35, 5 | Y | 11/8/2016 | Y | 10/4/2016 | Y | Y |  |  |  | Y
MI7220146 | ROSCOMMON HIGH SCHOOL | MI | LEAD SUMMARY | 0.0162 | 16.2 | 2017-01-01 | 2017-06-30 | 2017-09-08 07:55 | 2018-03-09 12:47 |  |  | Y | 1 - 21 ppb | Y | Y | Y | N | N | 5. None | 7.95-8.03 | NA | N | Y | Y |  | Pending | Sampled all DW locations, replaced. | Pending second round of samples.
MI7320187 | SAINT MICHAELS CHURCH | MI | LEAD SUMMARY | 0.017 | 17 | 2016-07-01 | 2016-12-31 | 2016-12-14 08:34 | 2018-03-09 12:47 |  | No | Y | 1 - 20 ppb | Y | Y | Y | Unknown | Unknown | 5. None | Unknown |  | N | N | Y |  | 2017 | Fixture Replacement |  |  |  |  | Y | Sep.-16 | N | 1, 20 | Y | 11/1/2016 | Y | 1/6/2017 | N | N |  | N |  | Y |  |  |  | Replaced fixture with elevated pb levels. Awaiting first round of semiannual monitoring.
MI7520157 | MICHIGAN MILK PRODUCERS ASSOC | MI | LEAD SUMMARY | 0.0181 | 18.1 | 2015-07-01 | 2015-12-31 | 2016-03-08 12:23 | 2018-03-09 12:47 |  |  | Y | 1 AT 37PPB | Y | Y | Y | N | N | 5. None | N | NA | Y | Y | Y |  | 43100 | Sampled all dw locations. Replaced offending fixture.
MI8020265 | COCA COLA REFRESHMENTS | MI | LEAD SUMMARY | 0.019 | 19 | 2014-01-01 | 2014-06-30 | 2014-08-26 17:19 | 2018-03-09 12:47 |  | Yes | [17 empty] | Based on PE responses, a PE (Type 65) violation should have been reported to SDWIS. Also, based on lead consumer notice responses, a LCR M&R (Type 66) violation should have been reported to SDWIS. | MDEQ 7/2017: For LCN (Type 66), 2016 was the first year of this requirement in NCWS Program; system eventually certified posting LCN 10/3/16. NCWS Program has no means of reporting Type 65 and 66 violations to SDWIS. | Based on responses to Questions 5 and 6, a PE (Type 65) violation should have been reported to SDWIS. Also, based on responses to Questions 7 and 8, a LCR (Type 66) violation should have been reported to SDWIS. | Y | May-14 | N | 16, 21 | N |  | N |  | N | N |  | N |  | N |  | 7/1/2015 |  | Still investigating, but two 6-month rounds of sampling in late 2015 and early 2016 resulted in lead and copper results well below the action levels.
MI8020265 | COCA COLA REFRESHMENTS | MI | LEAD SUMMARY | 0.0864 | 86.4 | 2012-01-01 | 2012-06-30 | 2012-08-29 10:29 | 2016-12-14 08:34 |  | Yes | [17 empty] | Based on PE responses, a PE (Type 65) violation should have been reported to SDWIS. Also, based on lead consumer notice responses, a LCR M&R (Type 66) violation should have been reported to SDWIS. | MDEQ 7/2017: For PE (Type 65), confirmation of PE was eventually received 12/28/2012; for LCN (Type 66), 2016 was the first year of this requirement in NCWS Program; system eventually certified posting LCN 10/3/16. NCWS Program has no means of reporting | Based on responses to Questions 5 and 6, a PE (Type 65) violation should have been reported to SDWIS. Also, based on responses to Questions 7 and 8, a LCR (Type 66) violation should have been reported to SDWIS. | Y | Jun-12 | N | 122, 33, 25 | Y | 12/28/2012 | N |  | N | N |  | N |  | Y |  | 1/1/2014 |  | Resolved
MI8020269 | BLOOMINGDALE HIGH SCHOOL | MI | LEAD SUMMARY | 0.20375 | 203.75 | 2014-07-01 | 2014-12-31 | 2016-12-14 08:34 | 2018-03-09 12:47 |  | Yes
MI8320059 | WEXFORD MISSAUKEE CAREER TECH CENTER | MI | LEAD SUMMARY | 0.0342 | 34.2 | 2007-07-01 | 2007-12-31 | 2008-02-27 12:33 | 2013-09-03 11:15 |  | Yes | [17 empty] | Based on responses to PE Questions, it appears a PE (Type 65) violation should have been entered into SDWIS. | MDEQ 7/2017: 2013 was first year of this requirement in Michigan for this system. Posted LCN 11/7/16. NCWS Program has no means of reporting Type 65 and 66 violations to SDWIS. | Based on responses to Questions 5 and 6, a PE (Type 65) violation should have been reported to SDWIS. | Y | Aug-07 | N | 95, 19 | N |  | N |  | N | N |  | N |  | Y |  | 1/1/2009 |  | Resolved

## 7. Dropdown List Values (hidden)
Number | Dropdown Value | Notes
1 | 1. PWS did not have a Pb ALE | i.e., a data entry error occurred in the data reported to SDWIS-Fed, but the actual Pb 90th Percentile does not exceed 15 ppb. (correcting these issues before the next quarterly freeze is strongly recommended)
2 | 2. PWS No Longer Subject to the Rule | i.e., the system is no longer a PWS (i.e., facility has closed or connected to another water source) or has been reclassified as a TNCWS
4 | 3. ALE Resolved with Sampling | i.e., 2 consecutive 6-month rounds were collected with 90th percentile Pb that does not exceed 15 ppb where the state does not have any knowledge of any tangible corrective action.
4 | 4. ALE Resolved with Corrective Action followed by Sampling | i.e., The system completed a tangible corrective action (e.g., replacement of fixture/plumbing at a NTNCWS or single-building CWS, improvements to sampling plans [e.g., to not sample non-consumption/vacant taps in future]), other than installing treatment, and 2 consecutive 6-month rounds of LCR tap sampling were subsequently collected with Pb 90th percentiles that do not exceed 15 ppb.
5 | 5. ALE Resolved with Treatment | i.e., Corrosion Control Treatment has been installed (or adjusted) and follow-up sampling has been completed, where 2 consecutive 6-month rounds were collected with 90th percentile Pb that does not exceed 15 ppb [see 40 CFR 141.81(e)(5) and (6) for small/medium systems]
6 | 6. ALE not Resolved – Conducting CCT Steps to Resolve with Treatment | i.e., the system is moving through the Corrosion Control Treatment steps as laid out in rule [see 40 CFR 141.81(e)(1) through (5) for small/medium systems]
7 | 7. ALE not Resolved – Awaiting Sample Results – No Results Reported Yet | i.e., System does not intend to pursue centralized treatment, but no LCR tap monitoring results are available yet with Pb 90th Percentile that does not exceed 15 ppb - Note: these systems should be submitting a corrosion control treatment recommendation (or equivalent), within 6 months of the ALE monitoring period [40 CFR 141.81(e) “Step 1” of the Treatment Steps and deadlines for small and medium-size systems: “A system exceeding the lead or copper action level shall recommend optimal corrosion control treatment (§141.82(a)) within six months after the end of the monitoring period during which it exceeds one of the action levels.” ]
8 | 8. ALE not Resolved – Awaiting Sample Results – Most Recent 6M Round does not exceed AL | i.e., Most recent 6-month round of LCR tap sampling was collected with Pb 90th percentile that does not exceed 15 ppb. Note: these systems should have submitted a corrosion control treatment recommendation (or equivalent), within 6 months of the ALE monitoring period [40 CFR 141.81(e) “Step 1” of the Treatment Steps and deadlines for small and medium-size systems: “A system exceeding the lead or copper action level shall recommend optimal corrosion control treatment (§141.82(a)) within six months after the end of the monitoring period during which it exceeds one of the action levels.”]
9 | 9. Other | [State to describe – this might include source water treatment, LSL replacement, etc.]

## ESRI_MAPINFO_SHEET (hidden)
DO NOT EDIT
For Esri use only