## BH
[7 empty] | Source Water Alkalinity | [5 empty] | Alternative Compliance Criteria (ACC) Rule 610c(1)(b)-(c)
Enhanced Coagulation/Softening Requirements | [5 empty] | Source TOC | 0-60 | >60-120 | >120 |  |  |  | - Source or Treated TOC RAA <2.0, OR
Supply: [name] | [5 empty] | >2.0-4.0 | 35% | 25% | 15% |  |  |  | - Source TOC RAA >4.0 & Alk RAA >60 AND
WSSN: 0600 | [5 empty] | >4.0-8.0 | 45% | 35% | 25% | jan |  |  | TTHM & HAA5 RAA <= 40/30 respectively, OR
[6 empty] | >8.0 | 50% | 40% | 30% |  |  |  | - TTHM & HAA5 <=40/30 & only Cl primary disinfectant…And more ACCs.
| A | B |  |  | C | D | E | F | G |  | H | I |  |  |  | May Reduce If Either …
| Treated TOC | Source TOC | Treated SUVA | Source SUVA | (1-A/B) x 100 | Source Water Alkalinity | Required TOC Removal | C/E Actual Removal | Credit 1.0 if Paired Sample Source or Treated | Credit 1.0 if RAA Source or Treated | Rem'l Ratio Quarterly | Rem'l Ratio RAA | Source TOC Qtly Ave | Source TOC RAA | Treated TOC Qtly Ave | 1 Yr Treated RAA <1.0 | 2 Yr Treated RAA <2.0 | Compliance with Treatment Technique (TT)
Month | (mg/L) | (mg/L) |  |  |  | (mg/L) | (%) | Ratio | TOC <2.0 | TOC <2.0 | [5 empty] | Rule 719e(4)(b)
January 2009
February 2009
March 2009 | 1.99 | 2.32 |  |  | 14.2241 |  | 25 | 0.56897 | 1 | 1 | 1 | 1 | 2.32 | 2.32 | 1.99 | 1.99 | 1.99 | Met ACC
April 2009
May 2009
June 2009 | 1.33 | 1.59 |  |  | 16.3522 | 102 | 25 | 0.65409 | 1 | 1 | 1 | 1 | 1.59 | 1.955 | 1.33 | 1.66 | 1.66 | Met ACC
July 2009
August 2009
September 2009 | 1.89 | 1.92 |  |  | 1.5625 | 112 | 25 | 0.0625 | 1 | 1 | 1 | 1 | 1.92 | 1.9433 | 1.89 | 1.7367 | 1.7367 | Met ACC
October 2009
November 2009 | 1.49 | 2.39 |  |  | 37.6569 | 129 | 15 | 2.5105 | 2.5105 | 2.5105
December 2009 | [10 empty] | 2.5105 | 1.3776 | 2.39 | 2.055 | 1.49 | 1.675 | 1.675 | Met ACC
January 2010
February 2010
March 2010 | 1.9 | 2.6 |  |  | 26.9231 | 130 | 15 | 1.7949 | 1.7949 | 1.7949 | 1.7949 | 1.5763 | 2.6 | 2.125 | 1.9 | 1.6525 | 1.72 | Met ACC
April 2010
May 2010
June 2010 | 2.1 | 2.5 |  |  | 16 | [5 empty] | M/R viol | 1.7684 | 2.5 | 2.3525 | 2.1 | 1.845 | 1.7833 | Met ACC
July 2010
August 2010 | 2 | 3 |  |  | 33.3333
September 2010 | [10 empty] | M/R viol | 2.1527 | 3 | 2.6225 | 2 | 1.8725 | 1.8143 | Met ACC
October 2010
November 2010
December 2010 | 1.5 | 3.2 |  |  | 53.125 | [5 empty] | M/R viol | 1.7949 | 3.2 | 2.825 | 1.5 | 1.875 | 1.775 | Met ACC
January 2011
February 2011
March 2011 | 1.94 | 2.82 |  |  | 31.2057 | [5 empty] | M/R viol | #DIV/0! | 2.82 | 2.88 | 1.94 | 1.885 | 1.7687 | Met ACC
April 2011
May 2011
June 2011 | 1.78 | 2.22 |  |  | 19.8198 | [5 empty] | M/R viol | #DIV/0! | 2.22 | 2.81 | 1.78 | 1.805 | 1.825 | Met ACC
July 2011
August 2011
September 2011 | 1.79 | 1.82 |  |  | 1.6484 | [5 empty] | M/R viol | #DIV/0! | 1.82 | 2.515 | 1.79 | 1.7525 | 1.8125 | Met ACC
October 2011 | [9 empty] | #DIV/0!
November 2011 | [9 empty] | #DIV/0!
December 2011 | BOTTLE BROKE IN TRANSIT - RESAMPLED IN JAN 2012 - NO VIOLATION ISSUED | [8 empty] | #DIV/0! | #DIV/0! | #DIV/0! |  | 2.2867 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
January 2012 | 2.14 | 2.18 |  |  | 1.8349 |  |  |  |  | #DIV/0!
February 2012 | 1.84 | 2.39 |  |  | 23.0126 |  |  |  |  | #DIV/0!
March 2012 | 1.86 | 2.85 |  |  | 34.7368 |  |  |  |  | #DIV/0! | #DIV/0! | #DIV/0! | 2.4733 | 2.1711 | 1.9467 | #DIV/0! | #DIV/0! | #DIV/0!
April 2012 | [9 empty] | #DIV/0!
May 2012 | 1.32 | 1.9 |  |  | 30.5263 |  |  |  |  | #DIV/0!
June 2012 | [9 empty] | #DIV/0! | #DIV/0! | #DIV/0! | 1.9 | 2.0644 | 1.32 | #DIV/0! | #DIV/0! | #DIV/0!
July 2012 | [9 empty] | #DIV/0!
August 2012 | [9 empty] | #DIV/0!
September 2012 | 1.44 | 1.76 |  |  | 18.1818 |  |  |  |  | #DIV/0! | #DIV/0! | #DIV/0! | 1.76 | 2.0444 | 1.44 | #DIV/0! | #DIV/0! | #DIV/0!
October 2012
November 2012 | 1.78 | 1.88 |  |  | 5.3191
December 2012 | 1.11 | 1.42 |  |  | 21.831 | [5 empty] | M/R viol | #DIV/0! | 1.65 | 1.9458 | 1.445 | 1.5379 | #DIV/0! | Met ACC
2013-01-01
2013-02-01
2013-03-01 | 1.36 | 1.64 |  |  | 17.0732 | 107 | 25 | 0.68293 | 1 | 1 | 1 | #DIV/0! | 1.64 | 1.7375 | 1.36 | 1.3913 | #DIV/0! | Met ACC
2013-04-01
2013-05-01
2013-06-01 | 1.2 | 1.47 |  |  | 18.3673 | 101 | 25 | 0.73469 | 1 | 1 | 1 | #DIV/0! | 1.47 | 1.63 | 1.2 | 1.3613 | #DIV/0! | Met ACC
2013-07-01
2013-08-01
2013-09-01 | 1.33 | 1.49 |  |  | 10.7383 | 104 | 25 | 0.42953 | 1 | 1 | 1 | 1 | 1.49 | 1.5625 | 1.33 | 1.3337 | #DIV/0! | Met ACC
2013-10-01
2013-11-01 | 1.28 | 1.59 |  |  | 19.4969 | 102 | 25 | 0.77987 | 1 | 1
2013-12-01 | [10 empty] | 1 | 1 | 1.59 | 1.5475 | 1.28 | 1.2925 | 1.4152 | Met ACC
2014-01-01
2014-02-01 | 2.88 | 3.83 |  |  | 24.8042 | 131 | 15 | 1.6536 | 1.6536 | 1.6536
2014-03-01 | [10 empty] | 1.6536 | 1.1634 | 3.83 | 2.095 | 2.88 | 1.6725 | 1.5319 | Met ACC
2014-04-01
2014-05-01 | 1.62 | 1.68 |  |  | 3.5714 | 111 | 25 | 0.14286 | 1 | 1
2014-06-01 | 1.38 | 1.57 |  |  | 12.1019 | 100 | 25 | 0.48408 | 1 | 1 | 1 | 1.1634 | 1.625 | 2.1338 | 1.5 | 1.7475 | 1.5544 | Met ACC
2014-07-01
2014-08-01
2014-09-01 | 1.34 | 1.54 |  |  | 12.987 | 108 | 25 | 0.51948 | 1 | 1 | 1 | 1.1634 | 1.54 | 2.1463 | 1.34 | 1.75 | 1.5419 | Met ACC
2014-10-01
2014-11-01 | 1.31 | 1.53 |  |  | 14.3791 | 106 | 25 | 0.57516 | 1 | 1
2014-12-01 | [6 empty] | 25 |  |  |  | 1 | 1.1634 | 1.53 | 2.1313 | 1.31 | 1.7575 | 1.525 | Met ACC
2015-01-01
2015-02-01 | 1.73 | 2.11 |  |  | 18.0095 | 129 | 15 | 1.2006 | 1.2006 | 1.2006
2015-03-01 | [10 empty] | 1.2006 | 1.0502 | 2.11 | 1.7012 | 1.73 | 1.47 | 1.5713 | Met ACC
2015-04-01
2015-05-01 | 1.27 | 1.67 |  |  | 23.9521
2015-06-01 | [10 empty] | M/R viol | 1.0669 | 1.67 | 1.7125 | 1.27 | 1.4125 | 1.58 | Met ACC
2015-07-01
2015-08-01 | 1.23 | 0.79 |  |  | -55.6962
2015-09-01 | 1.29 | 1.63 |  |  | 20.8589 | [5 empty] | M/R viol | 1.1003 | 1.21 | 1.63 | 1.26 | 1.3925 | 1.5713 | Met ACC
2015-10-01
2015-11-01 | 1.18 | 1.76 |  |  | 32.9545
2015-12-01 | [10 empty] | #DIV/0! | #DIV/0! | 1.76 | 1.6875 | 1.18 | 1.36 | 1.5587 | Met ACC
2016-01-01
2016-02-01 | [18 empty] | MON VIOL
2016-03-01 | [10 empty] | #DIV/0! | #DIV/0! |  | 1.5467 |  | 1.2367 | 1.37 | Met ACC
2016-04-01
2016-05-01 | 1.64 | 1.97 |  |  | 16.7513 | 111 | 25 | 0.67005 | 1 | 1
2016-06-01 | [10 empty] | 1 | #DIV/0! | 1.97 | 1.6467 | 1.64 | 1.36 | 1.39 | Met ACC
2016-07-01
2016-08-24 | 1.75 | 1.8 |  |  | 2.7778 | 106 | 25 | 0.11111 | 1 | 1
2016-09-01 | [10 empty] | 1 | #DIV/0! | 1.8 | 1.8433 | 1.75 | 1.5233 | 1.4486 | Met ACC
2016-10-01
2016-11-01
2016-12-22 | 1.36 | 1.45 |  |  | 6.2069 | 116 | 25 | 0.24828 | 1 | 1 | 1 | #DIV/0! | 1.45 | 1.74 | 1.36 | 1.5833 | 1.4557 | Met ACC
2017-01-01
2017-02-22 | 1.99 | 2.22 |  |  | 10.3604 | 105 | 25 | 0.41441 | 0.41441 | 0.41441 | [8 empty] | 2017-02-22
2017-03-01 | [10 empty] | 0.41441 | 0.8536 | 2.22 | 1.86 | 1.99 | 1.685 | 1.4929 | Met ACC
2017-04-01
2017-05-17 | 2.05 | 2.61 |  |  | 21.4559 | 118 | 25 | 0.85824 | 0.85824 | 1
2017-06-01 | [10 empty] | 0.85824 | 0.81816 | 2.61 | 2.02 | 2.05 | 1.7875 | 1.6043 | Met ACC
2017-07-01
2017-08-24 | 1.71 | 1.74 |  |  | 1.7241 | 113 | 25 | 0.068966 | 1 | 1
2017-09-01 | [10 empty] | 1 | 0.81816 | 1.74 | 2.005 | 1.71 | 1.7775 | 1.6686 | Met ACC
2017-10-01
2017-11-08 | 2.19 | 2.69 |  |  | 18.5874 | 107 | 25 | 0.74349 | 0.74349 | 1
2017-12-01 | [10 empty] | 0.74349 | 0.75404 | 2.69 | 2.315 | 2.19 | 1.985 | 1.8129 | Met ACC
2018-02-14 | 2.51 | 2.61 |  |  | 3.8314 | 134 | 15 | 0.25543 | 0.25543 | 1 | [8 empty] | 2017-02-22
[11 empty] | 0.25543 | 0.71429 | 2.61 | 2.4125 | 2.51 | 2.115 | 1.9 | TT viol?/See more ACC.
2018-04-26 | 2.5 | 2.51 |  |  | 0.39841 | 118 | 25 | 0.015936 | 0.015936 | 0.015936
2018-05-21 | 1.71 | 2.22 |  |  | 22.973 | 110 | 25 | 0.91892 | 1 | 1
2018-06-28 | 1.58 | 2.26 |  |  | 30.0885 | 105 | 25 | 1.2035 | 1.2035 | 1.2035 | 0.015936 | 0.50371 | 2.33 | 2.3425 | 1.93 | 2.085 | 1.9362 | TT viol?/See more ACC.
2018-07-26 | 1.76 | 1.99 |  |  | 11.5578 | 108 | 25 | 0.46231 | 1 | 1
2018-08-08 | 2.19 | 2.47 |  |  | 11.336 | 110 | 25 | 0.45344 | 0.45344 | 0.45344
missed | missed | [9 empty] | n/a | 0.33829 | 2.23 | 2.465 | 1.975 | 2.1512 | 1.9644 | TT viol?/See more ACC.
2018-10-30 | 1.6 | 1.88 |  | 0.9 | 14.8936 | 130 | 15 | 0.99291 | 1 | 1
2018-11-07 | 1.74 | 1.86 |  |  | 6.4516 | 111 | 25 | 0.25806 | 1 | 1
missed | missed | [9 empty] | 1 | 0.42379 | 1.87 | 2.26 | 1.67 | 2.0212 | 2.0031 | TT viol?/See more ACC.
state lab used
May 2018 DEQ sample was invalidated by the DEQ Laboratory due to not meeting thermal preservation requirements
June 2018 DEQ sample was invalidated by the DEQ Laboratory due to not meeting thermal preservation requirements
July 2018 DEQ sample was invalidated by the DEQ Laboratory due to not meeting thermal preservation requiremen
August 2018 DEQ sample was invalidated by the DEQ Laboratory due to not meeting thermal preservation requiremen
note: suva sample taken to eurofins in october.