## Sheet1
Carus 8600 | City of Benton Harbor |  | Corrosion Inhibitor Addition
Ortho Content | 70% | Poly Content | 30% | Density: | 11.4 | lbs/gal
Strength | 33% | total P
Chemical Use Flow Rate Calculation (gallons per day)
|  | Min Flow Rate | Ave Flow Rate | Max Flow Rate | State Rated Capacity
Plant Flow Rate (mgd): |  | 2 | 3 | 4 | 8
Chem Dosing Rate: | 1 mg/L as PO4 | 4.4338 | 6.6507 | 8.8676 | 17.7352 | 13.3014
| 2 mg/L as PO4 | 8.8676 | 13.3014 | 17.7352 | 35.4705
| 3 mg/L as PO4 | 13.3014 | 19.9522 | 26.6029 | 53.2057
Goal: | 1.5 | mg/L as PO4
Low End: | 9.3 | gpd
High end: | 37.5 | gpd
Proposed Pump: | 40 | gpd
Day Tank Use
| realistic day: | max day:
Gal Chem per day | 10 | 40
# days per tank | 5.5 | 1.375