## Sheet1
Benton Harbor Flushing/Sampling November 2020
The initial flushing on 11/7/2020 did not achieve the intended flow rates, hydrant flushing methods were revised and reflushed 11/8/2020 thru 11/9/2020
202 South Fair | Fair/Main | Empire/Colfax | Colfax/Britain | 295 Colfax
2020-11-08 | 2020-11-08 | 2020-11-08 | 2020-11-08 | 2020-11-08
Flush 9:35 am - 2:37 am | Flush 9:49 am - 2:48 pm | Flush 10:03 - 3:00pm | Flush 10:15 am - 3:10 pm | 10:22am - 3:15pm
CL2 1.54 ppm/1.60 ppm | CL2 1.04 ppm/1.76 ppm | Cl2 0.90 ppm/1.46 ppm | CL2 0.0 ppm/1.65 ppm | CL2 1.35 ppm/1.71 ppm
Coliform = Absent | Coliform = Absent | Coliform = Absent | Coliform = Absent | Coliform = Absent
2020-11-09 | 2020-11-09 | 2020-11-09 | 2020-11-09 | 2020-11-09
Flush +- 9:30 am - 1:15 pm | Flush +- 9:30 am 1:27 pm | Flush +- 9:30am - 1:49pm | Flush +- 9:30am - 1:49pm | Flush +- 9:30am -1:57pm
CL2 1:27 pm 1.60 ppm | Cl2 1.66 ppm | CL2 1.53 ppm | CL2 1.53 ppm | Cl2 1.57
Coliform = Absent | Coliform = Absent | Coliform = Absent | Coliform = Absent | Coliform = Absent
South East Quadrant Flushing and Sampling 11/11/2020
Milton/Cross | Emery/Columbus | Cross/Lavette
2020-11-11
Flush 9:30am - 2:00pm | Flush 9:30am - 2:00pm | Flush 9:30am - 2:00pm
CL2 1.24 ppm - 1.47 ppm | CL2 1.22 ppm - 1.21 ppm | CL2 1.16 ppm - 1.41 ppm
Coliform = Absent | Coliform = Absent | Coliform = Absent
Plant Chlorination
| CL2 applied Pre/Post Treatment | Plant Tap CL2 Residual Free/Total
2020-11-05 | 3.92 ppm/0.44 mgl | 1.68 mgl/1.78 mgl
2020-11-06 | 4.31 ppm/0.47 mgl | 1.96 mgl/1.97 mgl
2020-11-07 | 4.69 ppm/0.84 mgl | 2.24 mgl/2.24 mgl
2020-11-08 | 4.98 ppm/0.77 mgl | 2.15 mgl/2.21 mgl
2020-11-09 | 4.72 ppm/0.45 mgl | 1.95 mgl/2.12 mgl
2020-11-10 | 3.90ppm/0.32 mgl | 2.05 mgl/2.22 mgl
2020-11-11 | 3.87 ppm/0.58 mgl | 2.20 mgl/2.28 mgl